## Space Types
OS:SpaceType | [12 empty] | OS:People:Definition | [17 empty] | OS:DesignSpecification:OutdoorAir | [11 empty] | OS:ElectricEquipment:Definition | [9 empty] | OS:Lights:Definition | [8 empty] | OS:GasEquipment:Definition | [10 empty] | OS:SpaceInfiltration:DesignFlowRate | [10 empty] | OS:InternalMass:Definition
[8 empty] | OS:Rendering:Color | OS:Rendering:Color | OS:Rendering:Color | OS:SpaceType | OS:Schedule |  |  | OS:People:Definition |  |  |  |  | OS:Schedule | OS:Schedule | OS:Schedule | OS:People:Definition |  |  |  |  | OS:People:Definition |  | OS:Schedule |  | OS:DesignSpecification:OutdoorAir |  | OS:DesignSpecification:OutdoorAir |  |  | OS:DesignSpecification:OutdoorAir |  |  |  |  | OS:DesignSpecification:OutdoorAir |  | OS:ElectricEquipment:Definition | OS:ElectricEquipment:Definition | OS:ElectricEquipment:Definition | OS:ElectricEquipment:Definition |  |  |  | OS:ElectricEquipment:Definition | OS:Schedule |  | OS:Lights:Definition | OS:Lights:Definition | OS:Lights:Definition |  |  |  | OS:Lights:Definition | OS:Schedule |  |  | OS:GasEquipment:Definition | OS:GasEquipment:Definition | OS:GasEquipment:Definition | OS:GasEquipment:Definition |  |  |  | OS:GasEquipment:Definition | OS:Schedule |  | OS:SpaceInfiltration:DesignFlowRate | OS:SpaceInfiltration:DesignFlowRate |  |  |  |  | OS:SpaceInfiltration:DesignFlowRate | OS:Schedule |  |  | OS:InternalMass:Definition | OS:InternalMass:Definition | OS:InternalMass:Definition | OS:Material | OS:Material | OS:Material | OS:Material | OS:Material | OS:Material | OS:Material | OS:Material | OS:Construction and OS:Material |  |  |  |  | OS:InternalMass:Definition
CATEGORY | !- Standards Template | !- Standards Building Type | !- Standards Space Type | OpenStudio_Standards.xlsx | Code Year | State | Code | !- Rendering Red Value | !- Rendering Green Value | !- Rendering Blue Value | !- Name | Schedule Set !- Name | OCCUPANT DENSITY FT2/person | OCCUPANT DENSITY #/1000 FT2 | !- People per Space Floor Area {person/m2} | Sensible Heat Gain (Btu/h-person) | Sensible Heat Gain (W/person) | Latent Heat Gain (Btu/h-person) | Latent Heat Gain (W/person) | Summer Design Day Total Heat Gain (W/person) | Winter Design Day Total Heat Gain (W/person) | Default Day Total Heat Gain (W/person) | !- Sensible Heat Fraction | Source_1 | Additional Info_1 | Source_2 | Additional Info_2 | !- Name | !- Number of People Schedule Name | Occupancy Activity Schedule !- Name | PEOPLE OUTDOOR AIRFLOW RATE IN BREATHING ZONE Rp CFM/PERSON | !- Outdoor Air Flow per Person {m3/s-person} | AREA OUTDOOR AIRFLOW RATE IN BREATHING ZONE Ra CFM/FT2a | !- Outdoor Air Flow per Floor Area {m3/s-m2} | EXHAUST AIRFLOW RATE CFM/FT 2 | EXHAUST AIRFLOW RATE m3/s-m2 | !- Outdoor Air Flow Air Changes per Hour {1/hr} | Source_1 | Additional Info_1 | Source_2 | Additional Info_2 | !- Name | Default Power Density (W/ft2) | !- Watts per Space Floor Area {W/m2} | !- Fraction Latent | !- Fraction Radiant | !- Fraction Lost | Source_1 | Source_2 | Additional Info | !- Name | Electric Equipment Schedule | Default Power Density (W/ft2) | !- Watts per Space Floor Area {W/m2} | !- Fraction Radiant | !- Fraction Visible | Source_1 | Source_2 | Additional Info | !- Name | Lighting Schedule | Interior Gas Appliance Power Density (W/ft2) | Interior Gas Appliance Power Density (Btu/h-ft2) | !- Power per Zone Floor Area {W/m2} | !- Fraction Latent | !- Fraction Radiant | !- Fraction Lost | Source_1 | Source_2 | Additional Info | !- Name | Gas Equipment Schedule | Infiltration per Exterior Area (ft^3/min*ft^2 ext) | !- Air Changes per Hour {1/hr} | !- Flow per Exterior Surface Area {m3/s-m2} | Source_1 | Additional Info_1 | Source_2 | Additional Info_2 | !- Name | Infiltration Schedule | Building Type | Space Type | !- Surface Area {m2} | !- Surface Area per Space Floor Area {dimensionless} | !- Surface Area per Person {m2/person} | !- Roughness | !- Thickness {m} | !- Conductivity {W/m-K} | !- Density {kg/m3} | !- Specific Heat {J/kg-K} | !- Thermal Absorptance | !- Solar Absorptance | !- Visible Absorptance | !- Name | Source_1 | Additional Info_1 | Source_2 | Additional Info_2 | !- Name
d83d8e85-c973-43f1-8010-e8f36dc62725 | 464b7a91-abc0-48af-b607-07922fa703df | 789d7a7f-91a3-4dde-9310-9a74c14d32e5 | c3101f12-7b66-41ad-90b5-0c5afec65227 |  |  |  |  | bb3bf4f1-c80b-43b9-93a6-263313c59141 | f48c2a4a-3151-4163-b625-b93c6c227f62 | 35292a8f-2c31-428e-b12b-ecb42e41f30c | c318426a-e0cf-4c00-830e-9470f81507bb | 36715673-fabf-4b26-bcb3-54efccbcf6ca |  |  | 1f550d2e-d956-4855-8f6c-850193633ba2 |  |  |  |  | f70f21e0-e825-4f34-a3a0-3417ba47b289 | 0a44a70a-025f-4b95-b067-1905cd773228 | f3e926b6-9054-43e5-b214-72715fea5476 | 7e5f790a-2539-4f59-b04d-75858ff1caa0 |  |  |  |  | 0e52365f-0968-4865-98c8-5a391db72fe1 | 729982cd-0e35-4f56-90dd-aa3ce52c45a4 | 7c329b17-a9b9-429d-87d6-8d696bb1a0f1 |  | a791e0a0-108f-4ea5-ac55-ffbc9ef41f04 |  | 03d16ff5-015b-4c1f-89e1-fb9e8f3c323e |  |  | 41dd9f25-8df0-46e6-9f29-cceef9210ae8 |  |  |  |  | f8a27cd2-f746-4301-a112-59d13e40d78d |  | dd740279-a043-472e-9440-1247838bdebd | 93c3190c-58c6-4fa6-b31d-e972f017b622 | e7668a0e-eeeb-49fe-b68d-e4673ff0492f | 17a128c0-8bb3-42fe-8fa8-e9b6c9857c61 |  |  |  | 88a913cc-2e7a-402c-8f68-e04d9aea2bfe | 922e17af-4f99-4a08-92d5-c8797f685f91 |  | da106b8e-74c8-48ae-9585-c42116b2ba37 | 37274c8e-ef2a-4273-be16-1568ef1010d8 | 2f6014cb-8ffd-48ef-8c06-e2f22e8f09fb |  |  |  | 8cd22776-3059-4312-be9f-414a4cc9a5d4 | 06a4bb43-86fe-4d0d-b323-df7f797ddedf |  |  | 75657b05-6269-49ed-9dde-0685e47cd2e8 | d7a052b3-0fd2-4248-aceb-14699019a4a4 | fa38e540-d001-49d9-b3f1-d1a707fc1579 | 297cff0e-3751-4d1e-8c51-b492f8bae160 |  |  |  | 4478951e-a465-46c5-913d-bcea7a66cb2a | be6b6705-67ab-46ec-a6e5-80adf6c48c0a |  | 306e4282-557a-4c79-a31e-dbe513817f52 | 821df950-1005-42a1-bb71-94e21d06f843 |  |  |  |  | f0b3db32-813a-495e-9ca0-dde8056737c8 | 94e29b50-ba90-424a-98b8-c2dc37ad1d28 |  |  | 620be5d0-583e-43e9-b3de-0b70c7cf5176 | 953b161f-1acf-4fc3-a393-bdce6b3c5153 | b80aad76-63a0-4cbf-802e-5e89b172c4f9 | 1bd0cfbf-ead3-4e72-b15b-e4980f9b59db | dc1f4078-c6b5-4ccb-a537-4da64d413107 | cff5961c-e380-4d30-9a4d-0bfdf353115f | 5a6d7588-d7ab-4a8a-be29-d0e69477a2d9 | 51ff4529-089d-43c6-90c4-e6bdcb13b9fe | dc5451c6-9cf1-4680-bb77-8c264cd2f1ec | 50e1157d-9579-4ef9-b50e-099cefad7e0f | 2810bb86-71f1-4ece-94e6-b7427b2274ef | feb23d72-7ec3-4505-84ec-987e02009258 |  |  |  |  | 65c47774-d0bf-4ce9-ba77-1b1304459dc7
BA Automotive Facility | 2021_WA_BuildingCode | Automotive Facility | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Automotive Facility_2021WABuildingCode | BA Automotive Facility_2021WABuildingCodeScheduleSet | 143 | 6.993 | 0.075272 | 375 | 109.9062 | 625 | 183.177 | 293.0832 | 97 | 120 | 0.375 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Automotive FacilityPeopleDef | NECB-E-Occupancy | BA Automotive FacilityActivity |  |  | 0.25 | 0.00127 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Automotive FacilityVent | 0.50325 | 5.417 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Automotive FacilityElectricalEquipDef | NECB-E-Electric-Equipment | 0.64 | 6.889 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Automotive facility | Washington State Energy Code Commercial TABLE C405.4.2Automotive facilityLightingDef | NECB-E-Lighting | 0.22082 | 0.75342 | 8.1099 | 0 | 0.75 | 0.25 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 93%ThermEffRadiant | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Automotive FacilityGasEquipDef | NECB-E-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Automotive facility_WholeBuilding | PNNL-NECB 2011BA Automotive FacilityInfil | Always On | Automotive facility | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Convention Center | 2021_WA_BuildingCode | Convention Center | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Convention Center_2021WABuildingCode | BA Convention Center_2021WABuildingCodeScheduleSet | 20 | 50 | 0.5382 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Convention CenterPeopleDef | NECB-C-Occupancy | BA Convention CenterActivity |  |  | 0.31 | 0.0015748 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Convention CenterVent | 0.74761 | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Convention CenterElectricalEquipDef | NECB-C-Electric-Equipment | 0.64 | 6.889 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Convention center | Washington State Energy Code Commercial TABLE C405.4.2Convention centerLightingDef | NECB-C-Lighting | 0.0066914 | 0.022831 | 0.24575 | 0 | 0.75 | 0.25 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 93%ThermEffRadiant | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Convention CenterGasEquipDef | NECB-C-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Convention centre_WholeBuilding | PNNL-NECB 2011BA Convention CenterInfil | Always On | Convention centre | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Courthouse | 2021_WA_BuildingCode | Courthouse | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Courthouse_2021WABuildingCode | BA Courthouse_2021WABuildingCodeScheduleSet | 14 | 71.4286 | 0.76885 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA CourthousePeopleDef | NECB-A-Occupancy | BA CourthouseActivity |  |  | 0.41 | 0.0020828 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA CourthouseVent | 1.669 | 17.9649 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA CourthouseElectricalEquipDef | NECB-A-Electric-Equipment | 0.79 | 8.5036 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Court house | Washington State Energy Code Commercial TABLE C405.4.2Court houseLightingDef | NECB-A-Lighting | 0.050185 | 0.17123 | 1.8432 | 0.01 | 0.4 | 0.4 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 60%ThermEffProcess | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA CourthouseGasEquipDef | NECB-A-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Courthouse_WholeBuilding | PNNL-NECB 2011BA CourthouseInfil | Always On | Courthouse | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Dining: Bar Lounge/Leisure | 2021_WA_BuildingCode | Dining: Bar Lounge/Leisure | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Dining: Bar Lounge/Leisure_2021WABuildingCode | BA Dining: Bar Lounge/Leisure_2021WABuildingCodeScheduleSet | 10 | 100 | 1.0764 | 275 | 80.5979 | 275 | 80.5979 | 161.1958 | 97 | 120 | 0.5 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Dining: Bar Lounge/LeisurePeopleDef | NECB-B-Occupancy | BA Dining: Bar Lounge/LeisureActivity |  |  | 0.93 | 0.0047244 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Dining: Bar Lounge/LeisureVent | 1.3161 | 14.166 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Dining: Bar Lounge/LeisureElectricalEquipDef | NECB-B-Electric-Equipment | 0.79 | 8.5036 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Dining: Bar lounge/leisure | Washington State Energy Code Commercial TABLE C405.4.2Dining: Bar lounge/leisureLightingDef | NECB-B-Lighting | 5.139 | 17.5342 | 188.7386 | 0 | 0.75 | 0.25 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 93%ThermEffRadiant | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Dining: Bar Lounge/LeisureGasEquipDef | RestaurantFastFood BLDG_EQUIP_SCH | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Dining - bar/lounge_WholeBuilding | PNNL-NECB 2011BA Dining: Bar Lounge/LeisureInfil | Always On | Dining - bar/lounge | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Dining: Cafeteria/Fast Food | 2021_WA_BuildingCode | Dining: Cafeteria/Fast Food | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Dining: Cafeteria/Fast Food_2021WABuildingCode | BA Dining: Cafeteria/Fast Food_2021WABuildingCodeScheduleSet | 10 | 100 | 1.0764 | 275 | 80.5979 | 275 | 80.5979 | 161.1958 | 97 | 120 | 0.5 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Dining: Cafeteria/Fast FoodPeopleDef | NECB-B-Occupancy | BA Dining: Cafeteria/Fast FoodActivity |  |  | 0.93 | 0.0047244 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Dining: Cafeteria/Fast FoodVent | 1.3684 | 14.729 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Dining: Cafeteria/Fast FoodElectricalEquipDef | NECB-B-Electric-Equipment | 0.72 | 7.7501 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Dining: Cafeteria/fast food | Washington State Energy Code Commercial TABLE C405.4.2Dining: Cafeteria/fast foodLightingDef | NECB-B-Lighting | 5.139 | 17.5342 | 188.7386 | 0 | 0.75 | 0.25 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 93%ThermEffRadiant | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Dining: Cafeteria/Fast FoodGasEquipDef | RestaurantFastFood BLDG_EQUIP_SCH | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Dining - cafeteria_WholeBuilding | PNNL-NECB 2011BA Dining: Cafeteria/Fast FoodInfil | Always On | Dining - cafeteria | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Dining: Family | 2021_WA_BuildingCode | Dining: Family | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Dining: Family_2021WABuildingCode | BA Dining: Family_2021WABuildingCodeScheduleSet | 14 | 71.4286 | 0.76885 | 275 | 80.5979 | 275 | 80.5979 | 161.1958 | 97 | 120 | 0.5 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Dining: FamilyPeopleDef | NECB-B-Occupancy | BA Dining: FamilyActivity |  |  | 0.71 | 0.0036068 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Dining: FamilyVent | 1.263 | 13.5949 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Dining: FamilyElectricalEquipDef | NECB-B-Electric-Equipment | 0.71 | 7.6424 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Dining: Family | Washington State Energy Code Commercial TABLE C405.4.2Dining: FamilyLightingDef | NECB-B-Lighting | 5.139 | 17.5342 | 188.7386 | 0.05 | 0.4 | 0.4 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 60%ThermEffProcess | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA Dining: FamilyGasEquipDef | RestaurantSitDown BLDG_EQUIP_SCH | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Dining - family_WholeBuilding | PNNL-NECB 2011BA Dining: FamilyInfil | Always On | Dining - family | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Dormitory | 2021_WA_BuildingCode | Dormitory | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Dormitory_2021WABuildingCode | BA Dormitory_2021WABuildingCodeScheduleSet | 100 | 10 | 0.10764 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA DormitoryPeopleDef | NECB-G-Occupancy | BA DormitoryActivity |  |  | 0.11 | 0.0005588 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA DormitoryVent | 1.9561 | 21.0558 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA DormitoryElectricalEquipDef | NECB-G-Electric-Equipment | 0.46 | 4.9514 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Dormitory | Washington State Energy Code Commercial TABLE C405.4.2DormitoryLightingDef | NECB-G-Lighting | 0.20409 | 0.69635 | 7.4955 | 0.01 | 0.4 | 0.4 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 60%ThermEffProcess | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA DormitoryGasEquipDef | ApartmentMidRise EQP_APT_SCH | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Dormitory_WholeBuilding | PNNL-NECB 2011BA DormitoryInfil | Always On | Dormitory | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Exercise Center | 2021_WA_BuildingCode | Exercise Center | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Exercise Center_2021WABuildingCode | BA Exercise Center_2021WABuildingCodeScheduleSet | 100 | 10 | 0.10764 | 710 | 208.0891 | 1090 | 319.4607 | 527.5498 | 97 | 120 | 0.39444 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Exercise CenterPeopleDef | NECB-B-Occupancy | BA Exercise CenterActivity |  |  | 0.26 | 0.0013208 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Exercise CenterVent | 0.67425 | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Exercise CenterElectricalEquipDef | NECB-B-Electric-Equipment | 0.67 | 7.2119 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Exercise center | Washington State Energy Code Commercial TABLE C405.4.2Exercise centerLightingDef | NECB-B-Lighting | 0.0066914 | 0.022831 | 0.24575 | 0.05 | 0.4 | 0.4 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 60%ThermEffProcess | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA Exercise CenterGasEquipDef | HotelSmall ExerciseCenter_Eqp_Sch | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Exercise centre_WholeBuilding | PNNL-NECB 2011BA Exercise CenterInfil | Always On | Exercise centre | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Fire Station | 2021_WA_BuildingCode | Fire Station | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Fire Station_2021WABuildingCode | BA Fire Station_2021WABuildingCodeScheduleSet | 33 | 30.303 | 0.32618 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Fire StationPeopleDef | NECB-F-Occupancy | BA Fire StationActivity |  |  | 0.21 | 0.0010668 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Fire StationVent | 1.5404 | 16.5804 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Fire StationElectricalEquipDef | NECB-F-Electric-Equipment | 0.54 | 5.8126 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Fire station | Washington State Energy Code Commercial TABLE C405.4.2Fire stationLightingDef | NECB-F-Lighting | 0.22082 | 0.75342 | 8.1099 | 0 | 0.75 | 0.25 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 93%ThermEffRadiant | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Fire StationGasEquipDef | NECB-F-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Fire station_WholeBuilding | PNNL-NECB 2011BA Fire StationInfil | Always On | Fire station | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Gymnasium | 2021_WA_BuildingCode | Gymnasium | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Gymnasium_2021WABuildingCode | BA Gymnasium_2021WABuildingCodeScheduleSet | 33 | 30.303 | 0.32618 | 710 | 208.0891 | 1090 | 319.4607 | 527.5498 | 97 | 120 | 0.39444 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA GymnasiumPeopleDef | NECB-B-Occupancy | BA GymnasiumActivity |  |  | 0.3 | 0.001524 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA GymnasiumVent | 0.67425 | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA GymnasiumElectricalEquipDef | NECB-B-Electric-Equipment | 0.75 | 8.073 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Gymnasium | Washington State Energy Code Commercial TABLE C405.4.2GymnasiumLightingDef | NECB-B-Lighting | 0.0066914 | 0.022831 | 0.24575 | 0 | 0.75 | 0.25 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 93%ThermEffRadiant | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA GymnasiumGasEquipDef | SchoolSecondary BLDG_EQUIP_SCH | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Gymnasium_WholeBuilding | PNNL-NECB 2011BA GymnasiumInfil | Always On | Gymnasium | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Healthcare Clinic | 2021_WA_BuildingCode | Healthcare Clinic | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Healthcare Clinic_2021WABuildingCode | BA Healthcare Clinic_2021WABuildingCodeScheduleSet | 200 | 5 | 0.05382 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Healthcare ClinicPeopleDef | NECB-A-Occupancy | BA Healthcare ClinicActivity |  |  | 0.47 | 0.0023876 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Healthcare ClinicVent | 1.2202 | 13.1339 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Healthcare ClinicElectricalEquipDef | NECB-A-Electric-Equipment | 0.7 | 7.5348 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Health care clinic | Washington State Energy Code Commercial TABLE C405.4.2Health care clinicLightingDef | NECB-A-Lighting | 0.33122 | 1.1301 | 12.1648 | 0 | 0 | 0.5 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | DOEPrototype | COMNET-REV9California Commercial End-Use Survey (CEUS)DOEPrototypeBA Healthcare ClinicGasEquipDef | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Health-care clinic_WholeBuilding | PNNL-NECB 2011BA Healthcare ClinicInfil | Always On | Health-care clinic | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Hospital | 2021_WA_BuildingCode | Hospital | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Hospital_2021WABuildingCode | BA Hospital_2021WABuildingCodeScheduleSet | 200 | 5 | 0.05382 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA HospitalPeopleDef | NECB-H-Occupancy | BA HospitalActivity |  |  | 0.47 | 0.0023876 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA HospitalVent | 1.2488 | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA HospitalElectricalEquipDef | NECB-H-Electric-Equipment | 0.84 | 9.0418 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Hospital | Washington State Energy Code Commercial TABLE C405.4.2HospitalLightingDef | NECB-H-Lighting | 0.33122 | 1.1301 | 12.1648 | 0.01 | 0.2 | 0.7 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | DOEPrototype | COMNET-REV9California Commercial End-Use Survey (CEUS)DOEPrototypeBA HospitalGasEquipDef | Hospital BLDG_EQUIP_SCH | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Hospital_WholeBuilding | PNNL-NECB 2011BA HospitalInfil | Always On | Hospital | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Hotel | 2021_WA_BuildingCode | Hotel | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Hotel_2021WABuildingCode | BA Hotel_2021WABuildingCodeScheduleSet | 250 | 4 | 0.043056 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA HotelPeopleDef | NECB-F-Occupancy | BA HotelActivity |  |  | 0.08 | 0.0004064 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA HotelVent | 1.5641 | 16.8363 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA HotelElectricalEquipDef | NECB-F-Electric-Equipment | 0.56 | 6.0278 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Hotel | Washington State Energy Code Commercial TABLE C405.4.2HotelLightingDef | NECB-F-Lighting | 0.20409 | 0.69635 | 7.4955 | 0 | 0.5 | 0 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | DOEPrototype | COMNET-REV9California Commercial End-Use Survey (CEUS)DOEPrototypeBA HotelGasEquipDef | HotelLarge BLDG_EQUIP_SCH | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Hotel_WholeBuilding | PNNL-NECB 2011BA HotelInfil | Always On | Hotel | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Library | 2021_WA_BuildingCode | Library | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Library_2021WABuildingCode | BA Library_2021WABuildingCodeScheduleSet | 100 | 10 | 0.10764 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA LibraryPeopleDef | NECB-C-Occupancy | BA LibraryActivity |  |  | 0.11 | 0.0005588 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA LibraryVent | 0.93723 | 10.0883 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA LibraryElectricalEquipDef | NECB-C-Electric-Equipment | 0.83 | 8.9341 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Library | Washington State Energy Code Commercial TABLE C405.4.2LibraryLightingDef | NECB-C-Lighting | 0.0066914 | 0.022831 | 0.24575 | 0.01 | 0.4 | 0.4 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 60%ThermEffProcess | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA LibraryGasEquipDef | NECB-C-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Library_WholeBuilding | PNNL-NECB 2011BA LibraryInfil | Always On | Library | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Manufacturing Facility | 2021_WA_BuildingCode | Manufacturing Facility | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Manufacturing Facility_2021WABuildingCode | BA Manufacturing Facility_2021WABuildingCodeScheduleSet | 143 | 6.993 | 0.075272 | 580 | 169.9883 | 870 | 254.9824 | 424.9707 | 97 | 120 | 0.4 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Manufacturing FacilityPeopleDef | NECB-A-Occupancy | BA Manufacturing FacilityActivity |  |  | 0.25 | 0.00127 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Manufacturing FacilityVent | 0.34481 | 3.7116 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Manufacturing FacilityElectricalEquipDef | NECB-A-Electric-Equipment | 0.82 | 8.8265 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Manufacturing facility | Washington State Energy Code Commercial TABLE C405.4.2Manufacturing facilityLightingDef | NECB-A-Lighting | 0.22082 | 0.75342 | 8.1099 | 0 | 0.75 | 0.25 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 93%ThermEffRadiant | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Manufacturing FacilityGasEquipDef | NECB-A-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Manufacturing facility_WholeBuilding | PNNL-NECB 2011BA Manufacturing FacilityInfil | Always On | Manufacturing facility | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Motel | 2021_WA_BuildingCode | Motel | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Motel_2021WABuildingCode | BA Motel_2021WABuildingCodeScheduleSet | 250 | 4 | 0.043056 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA MotelPeopleDef | NECB-F-Occupancy | BA MotelActivity |  |  | 0.08 | 0.0004064 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA MotelVent | 1.5641 | 16.8363 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA MotelElectricalEquipDef | NECB-F-Electric-Equipment | 0.56 | 6.0278 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Hotel | Washington State Energy Code Commercial TABLE C405.4.2HotelLightingDef | NECB-F-Lighting | 0.20409 | 0.69635 | 7.4955 | 0.01 | 0.4 | 0.4 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 60%ThermEffProcess | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA MotelGasEquipDef | NECB-F-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Motel_WholeBuilding | PNNL-NECB 2011BA MotelInfil | Always On | Motel | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Motion Picture Theater | 2021_WA_BuildingCode | Motion Picture Theater | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Motion Picture Theater_2021WABuildingCode | BA Motion Picture Theater_2021WABuildingCodeScheduleSet | 7 | 142.8571 | 1.5377 | 225 | 65.9437 | 105 | 30.7737 | 96.7175 | 97 | 120 | 0.68182 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Motion Picture TheaterPeopleDef | NECB-C-Occupancy | BA Motion Picture TheaterActivity |  |  | 1.19 | 0.0060452 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Motion Picture TheaterVent | 0.74485 | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Motion Picture TheaterElectricalEquipDef | NECB-C-Electric-Equipment | 0.44 | 4.7362 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Motion picture theater | Washington State Energy Code Commercial TABLE C405.4.2Motion picture theaterLightingDef | NECB-C-Lighting | 0.0066914 | 0.022831 | 0.24575 | 0.01 | 0.4 | 0.4 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 60%ThermEffProcess | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA Motion Picture TheaterGasEquipDef | NECB-C-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Motion picture theatre_WholeBuilding | PNNL-NECB 2011BA Motion Picture TheaterInfil | Always On | Motion picture theatre | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Multifamily | 2021_WA_BuildingCode | Multifamily | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Multifamily_2021WABuildingCode | BA Multifamily_2021WABuildingCodeScheduleSet | 380 | 2.6316 | 0.028326 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA MultifamilyPeopleDef | NECB-G-Occupancy | BA MultifamilyActivity |  |  | 0.06 | 0.0003048 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA MultifamilyVent | 1.4245 | 15.3331 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA MultifamilyElectricalEquipDef | NECB-G-Electric-Equipment | 0.41 | 4.4132 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Multiple family | Washington State Energy Code Commercial TABLE C405.4.2Multiple familyLightingDef | NECB-G-Lighting | 0.20409 | 0.69635 | 7.4955 | 0.01 | 0.4 | 0.4 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 60%ThermEffProcess | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA MultifamilyGasEquipDef | NECB-G-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Multi-unit residential_WholeBuilding | PNNL-NECB 2011BA MultifamilyInfil | Always On | Multi-unit residential | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Museum | 2021_WA_BuildingCode | Museum | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Museum_2021WABuildingCode | BA Museum_2021WABuildingCodeScheduleSet | 25 | 40 | 0.43056 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA MuseumPeopleDef | NECB-C-Occupancy | BA MuseumActivity |  |  | 0.36 | 0.0018288 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA MuseumVent | 0.74485 | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA MuseumElectricalEquipDef | NECB-C-Electric-Equipment | 0.55 | 5.9202 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Museum | Washington State Energy Code Commercial TABLE C405.4.2MuseumLightingDef | NECB-C-Lighting | 0.0066914 | 0.022831 | 0.24575 | 0 | 0.75 | 0.25 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 93%ThermEffRadiant | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA MuseumGasEquipDef | NECB-A-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Museum_WholeBuilding | PNNL-NECB 2011BA MuseumInfil | Always On | Museum | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Office | 2021_WA_BuildingCode | Office | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Office_2021WABuildingCode | BA Office_2021WABuildingCodeScheduleSet | 200 | 5 | 0.05382 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA OfficePeopleDef | NECB-A-Occupancy | BA OfficeActivity |  |  | 0.09 | 0.0004572 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA OfficeVent | 1.6721 | 17.9987 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA OfficeElectricalEquipDef | NECB-A-Electric-Equipment | 0.64 | 6.889 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Office | Washington State Energy Code Commercial TABLE C405.4.2OfficeLightingDef | NECB-A-Lighting | 0.036803 | 0.12557 | 1.3516 | 0.01 | 0.4 | 0.4 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 60%ThermEffProcess | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA OfficeGasEquipDef | OfficeMedium BLDG_EQUIP_SCH | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Office_WholeBuilding | PNNL-NECB 2011BA OfficeInfil | Always On | Office | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Parking Garage | 2021_WA_BuildingCode | Parking Garage | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Parking Garage_2021WABuildingCode | BA Parking Garage_2021WABuildingCodeScheduleSet | [30 empty] | 0.3 | 3.2292 | 0 | 0.06 | 0.88 |  | Medium Estimate: Workplace, 20% of Spaces with Level 2 Charger12%lost to heat | DOEPrototype | Medium Estimate: Workplace, 20% of Spaces with Level 2 Charger12%lost to heatDOEPrototypeBA Parking GarageElectricalEquipDef | NECB-H-Electric-Equipment | 0.14 | 1.507 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Parking garage | Washington State Energy Code Commercial TABLE C405.4.2Parking garageLightingDef | NECB-H-Lighting | 0 | 0 | 0 | 0 | 0.75 | 0.25 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 93%ThermEffRadiant | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Parking GarageGasEquipDef | NECB-H-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Parking garage_WholeBuilding | PNNL-NECB 2011BA Parking GarageInfil | Always On | Parking garage | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Penitentiary | 2021_WA_BuildingCode | Penitentiary | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Penitentiary_2021WABuildingCode | BA Penitentiary_2021WABuildingCodeScheduleSet | 40 | 25 | 0.2691 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA PenitentiaryPeopleDef | NECB-H-Occupancy | BA PenitentiaryActivity |  |  | 0.25 | 0.00127 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA PenitentiaryVent | 1.4928 | 16.0688 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA PenitentiaryElectricalEquipDef | NECB-H-Electric-Equipment | 0.65 | 6.9966 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Penitentiary | Washington State Energy Code Commercial TABLE C405.4.2PenitentiaryLightingDef | NECB-H-Lighting | 0.20409 | 0.69635 | 7.4955 | 0 | 0.75 | 0.25 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 93%ThermEffRadiant | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA PenitentiaryGasEquipDef | NECB-D-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Penitentiary_WholeBuilding | PNNL-NECB 2011BA PenitentiaryInfil | Always On | Penitentiary | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Performing Arts Theater | 2021_WA_BuildingCode | Performing Arts Theater | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Performing Arts Theater_2021WABuildingCode | BA Performing Arts Theater_2021WABuildingCodeScheduleSet | 14 | 71.4286 | 0.76885 | 225 | 65.9437 | 105 | 30.7737 | 96.7175 | 97 | 120 | 0.68182 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Performing Arts TheaterPeopleDef | NECB-C-Occupancy | BA Performing Arts TheaterActivity |  |  | 0.76 | 0.0038608 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Performing Arts TheaterVent | 0.74485 | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Performing Arts TheaterElectricalEquipDef | NECB-C-Electric-Equipment | 0.84 | 9.0418 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Performing arts theater | Washington State Energy Code Commercial TABLE C405.4.2Performing arts theaterLightingDef | NECB-C-Lighting | 0.0066914 | 0.022831 | 0.24575 | 0.01 | 0.4 | 0.4 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 60%ThermEffProcess | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA Performing Arts TheaterGasEquipDef | NECB-C-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Performing arts theatre_WholeBuilding | PNNL-NECB 2011BA Performing Arts TheaterInfil | Always On | Performing arts theatre | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Police Station | 2021_WA_BuildingCode | Police Station | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Police Station_2021WABuildingCode | BA Police Station_2021WABuildingCodeScheduleSet | 33 | 30.303 | 0.32618 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Police StationPeopleDef | NECB-H-Occupancy | BA Police StationActivity |  |  | 0.21 | 0.0010668 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Police StationVent | 1.5404 | 16.5804 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Police StationElectricalEquipDef | NECB-H-Electric-Equipment | 0.66 | 7.1042 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Police station | Washington State Energy Code Commercial TABLE C405.4.2Police stationLightingDef | NECB-H-Lighting | 0.22082 | 0.75342 | 8.1099 | 0 | 0.75 | 0.25 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 93%ThermEffRadiant | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Police StationGasEquipDef | NECB-H-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Police station_WholeBuilding | PNNL-NECB 2011BA Police StationInfil | Always On | Police station | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Post Office | 2021_WA_BuildingCode | Post Office | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Post Office_2021WABuildingCode | BA Post Office_2021WABuildingCodeScheduleSet | 33 | 30.303 | 0.32618 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Post OfficePeopleDef | NECB-A-Occupancy | BA Post OfficeActivity |  |  | 0.21 | 0.0010668 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Post OfficeVent | 0.90907 | 9.7853 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Post OfficeElectricalEquipDef | NECB-A-Electric-Equipment | 0.65 | 6.9966 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Post office | Washington State Energy Code Commercial TABLE C405.4.2Post officeLightingDef | NECB-A-Lighting | 0.22082 | 0.75342 | 8.1099 | 0 | 0.75 | 0.25 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 93%ThermEffRadiant | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Post OfficeGasEquipDef | NECB-A-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Post office_WholeBuilding | PNNL-NECB 2011BA Post OfficeInfil | Always On | Post office | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Religious Building | 2021_WA_BuildingCode | Religious Building | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Religious Building_2021WABuildingCode | BA Religious Building_2021WABuildingCodeScheduleSet | 8 | 125 | 1.3455 | 245 | 71.8054 | 155 | 45.4279 | 117.2333 | 97 | 120 | 0.6125 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Religious BuildingPeopleDef | NECB-I-Occupancy | BA Religious BuildingActivity |  |  | 0.66 | 0.0033528 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Religious BuildingVent | 0.29845 | 3.2125 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Religious BuildingElectricalEquipDef | NECB-I-Electric-Equipment | 0.67 | 7.2119 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Religious building | Washington State Energy Code Commercial TABLE C405.4.2Religious buildingLightingDef | NECB-I-Lighting | 0.0066914 | 0.022831 | 0.24575 | 0.03 | 0.4 | 0.4 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 60%ThermEffProcess | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA Religious BuildingGasEquipDef | NECB-I-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Religious_WholeBuilding | PNNL-NECB 2011BA Religious BuildingInfil | Always On | Religious | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Retail | 2021_WA_BuildingCode | Retail | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Retail_2021WABuildingCode | BA Retail_2021WABuildingCodeScheduleSet | 67 | 14.9254 | 0.16066 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA RetailPeopleDef | NECB-C-Occupancy | BA RetailActivity |  |  | 0.23 | 0.0011684 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA RetailVent | 0.70235 | 7.5601 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA RetailElectricalEquipDef | NECB-C-Electric-Equipment | 0.84 | 9.0418 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Retail | Washington State Energy Code Commercial TABLE C405.4.2RetailLightingDef | NECB-C-Lighting | 0.026766 | 0.091324 | 0.98301 | 0.01 | 0.4 | 0.4 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 60%ThermEffProcess | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA RetailGasEquipDef | RetailStandalone BLDG_EQUIP_SCH | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Retail_WholeBuilding | PNNL-NECB 2011BA RetailInfil | Always On | Retail | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA School/University | 2021_WA_BuildingCode | School/University | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA School/University_2021WABuildingCode | BA School/University_2021WABuildingCodeScheduleSet | 40 | 25 | 0.2691 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA School/UniversityPeopleDef | NECB-D-Occupancy | BA School/UniversityActivity |  |  | 0.47 | 0.0023876 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA School/UniversityVent | 0.68748 | 7.4001 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA School/UniversityElectricalEquipDef | NECB-D-Electric-Equipment | 0.7 | 7.5348 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | School/university | Washington State Energy Code Commercial TABLE C405.4.2School/universityLightingDef | NECB-D-Lighting | 0.040148 | 0.13699 | 1.4745 | 0.01 | 0.4 | 0.4 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 60%ThermEffProcess | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA School/UniversityGasEquipDef | SchoolSecondary BLDG_EQUIP_SCH | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | School/university_WholeBuilding | PNNL-NECB 2011BA School/UniversityInfil | Always On | School/university | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Sports Arena | 2021_WA_BuildingCode | Sports Arena | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Sports Arena_2021WABuildingCode | BA Sports Arena_2021WABuildingCodeScheduleSet | [20 empty] | 0.3 | 0.001524 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Sports ArenaVent | 0.74761 | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Sports ArenaElectricalEquipDef | NECB-B-Electric-Equipment | 0.62 | 6.6737 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Sports arena | Washington State Energy Code Commercial TABLE C405.4.2Sports arenaLightingDef | NECB-B-Lighting | 0.0066914 | 0.022831 | 0.24575 | 0 | 0.75 | 0.25 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 93%ThermEffRadiant | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Sports ArenaGasEquipDef | NECB-B-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Sports arena_WholeBuilding | PNNL-NECB 2011BA Sports ArenaInfil | Always On | Sports arena | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Town Hall | 2021_WA_BuildingCode | Town Hall | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Town Hall_2021WABuildingCode | BA Town Hall_2021WABuildingCodeScheduleSet | 200 | 5 | 0.05382 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Town HallPeopleDef | NECB-D-Occupancy | BA Town HallActivity |  |  | 0.09 | 0.0004572 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA Town HallVent | 0.74761 | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Town HallElectricalEquipDef | NECB-D-Electric-Equipment | 0.69 | 7.4272 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Town hall | Washington State Energy Code Commercial TABLE C405.4.2Town hallLightingDef | NECB-D-Lighting | 0.036803 | 0.12557 | 1.3516 | 0.01 | 0.4 | 0.4 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 60%ThermEffProcess | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA Town HallGasEquipDef | NECB-D-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Town hall_WholeBuilding | PNNL-NECB 2011BA Town HallInfil | Always On | Town hall | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Transportation | 2021_WA_BuildingCode | Transportation | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Transportation_2021WABuildingCode | BA Transportation_2021WABuildingCodeScheduleSet | 10 | 100 | 1.0764 | 225 | 65.9437 | 105 | 30.7737 | 96.7175 | 97 | 120 | 0.68182 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA TransportationPeopleDef | NECB-H-Occupancy | BA TransportationActivity |  |  | 0.81 | 0.0041148 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA TransportationVent | 0.51912 | 5.5878 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA TransportationElectricalEquipDef | NECB-H-Electric-Equipment | 0.5 | 5.382 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Transportation | Washington State Energy Code Commercial TABLE C405.4.2TransportationLightingDef | NECB-H-Lighting | 0.0066914 | 0.022831 | 0.24575 | 0 | 0.75 | 0.25 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 93%ThermEffRadiant | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA TransportationGasEquipDef | NECB-H-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Transportation_WholeBuilding | PNNL-NECB 2011BA TransportationInfil | Always On | Transportation | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Warehouse | 2021_WA_BuildingCode | Warehouse | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Warehouse_2021WABuildingCode | BA Warehouse_2021WABuildingCodeScheduleSet | [20 empty] | 0.06 | 0.0003048 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA WarehouseVent | 0.30231 | 3.254 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA WarehouseElectricalEquipDef | NECB-A-Electric-Equipment | 0.4 | 4.3056 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Warehouse | Washington State Energy Code Commercial TABLE C405.4.2WarehouseLightingDef | NECB-A-Lighting | 0 | 0 | 0 | 0 | 0.75 | 0.25 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 93%ThermEffRadiant | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA WarehouseGasEquipDef | NECB-A-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Warehouse_WholeBuilding | PNNL-NECB 2011BA WarehouseInfil | Always On | Warehouse | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Workshop | 2021_WA_BuildingCode | Workshop | Whole Building | WholeBuilding | 2021 | WA | BuildingCode | 255 | 255 | 255 | BA Workshop_2021WABuildingCode | BA Workshop_2021WABuildingCodeScheduleSet | 143 | 6.993 | 0.075272 | 635 | 186.1079 | 965 | 282.8253 | 468.9332 | 97 | 120 | 0.39688 | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA WorkshopPeopleDef | NECB-A-Occupancy | BA WorkshopActivity |  |  | 0.25 | 0.00127 |  |  |  | COMNET-REV9 | WholeBuilding |  |  | COMNET-REV9WholeBuildingBA WorkshopVent | 0.42834 | 4.6106 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA WorkshopElectricalEquipDef | NECB-A-Electric-Equipment | 0.91 | 9.7952 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Workshop | Washington State Energy Code Commercial TABLE C405.4.2WorkshopLightingDef | NECB-A-Lighting | 0.22082 | 0.75342 | 8.1099 | 0 | 0.75 | 0.25 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | 93%ThermEffRadiant | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA WorkshopGasEquipDef | NECB-A-Electric-Equipment | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Workshop_WholeBuilding | PNNL-NECB 2011BA WorkshopInfil | Always On | Workshop | WholeBuilding |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-Buildings |  |  | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
CS Audience Seating Area - Auditorium | 2021_WA_BuildingCode | Auditorium | Audience Seating Area | Auditorium | 2021 | WA | BuildingCode | 230 | 196 | 120 | CS Audience Seating Area - Auditorium_2021WABuildingCode | CS Audience Seating Area - Auditorium_2021WABuildingCodeScheduleSet | 6.6667 | 150 | 1.6146 | 225 | 65.9437 | 105 | 30.7737 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Auditoriums | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsCOMNET-REV9PeopleDef | SchoolSecondary BLDG_OCC_SCH_Auditorium | CS Audience Seating Area - AuditoriumActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Auditoriums |  |  | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsVent | 0.74761 | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - AuditoriumElectricalEquipDef | SchoolSecondary BLDG_EQUIP_SCH | 0.61 | 6.566 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Audience/seating area - Permanent - In an auditorium | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - In an auditoriumLightingDef | SchoolSecondary BLDG_LIGHT_SCH | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | SecondarySchool_Auditorium | PNNL-90.1-2013DOE_PrototypeSecondarySchool_AuditoriumInfil | SchoolSecondary INFIL_SCH_PNNL | SecondarySchool | Auditorium |  | 2.11 |  | MediumRough | 0.0332 | 0.966 | 219 | 859 | 0.9 | 0.65 | 0.65 | Mixed_AudienceSeating_Auditorium_33mm | CalculatedEstimate | FoldingUpholsteredSeatsWithSteelPedestals |  | Mixed_AudienceSeating_Auditorium_33mm | CalculatedEstimateFoldingUpholsteredSeatsWithSteelPedestalsMixed_AudienceSeating_Auditorium_33mmInternalMassDef
CS Audience Seating Area - Convention Center | 2021_WA_BuildingCode | Convention Center | Audience Seating Area | Convention centre - audience | 2021 | WA | BuildingCode | 230 | 196 | 120 | CS Audience Seating Area - Convention Center_2021WABuildingCode | CS Audience Seating Area - Convention Center_2021WABuildingCodeScheduleSet | 6.6667 | 150 | 1.6146 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Auditoriums | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsCOMNET-REV9PeopleDef | NECB-C-Occupancy | CS Audience Seating Area - Convention CenterActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Auditoriums |  |  | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsVent | 0.74761 | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - Convention CenterElectricalEquipDef | NECB-C-Electric-Equipment | 0.23 | 2.4757 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Audience/seating area - Permanent - Otherwise | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - OtherwiseLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Convention centre - audience | PNNL-NECB 2011DOE_PrototypeSpace Function_Convention centre - audienceInfil | Always On | Space Function | Convention centre - audience |  | 1.05 |  | MediumRough | 0.0084 | 3.73 | 636 | 562 | 0.9 | 0.7 | 0.7 | Mixed_AudienceSeating_ConventionCenter_8mm | CalculatedEstimate | PortableStackingConferenceChairs |  | Mixed_AudienceSeating_ConventionCenter_8mm | CalculatedEstimatePortableStackingConferenceChairsMixed_AudienceSeating_ConventionCenter_8mmInternalMassDef
CS Audience Seating Area - Exercise Center | 2021_WA_BuildingCode | Exercise Center | Audience Seating Area | Gym - audience | 2021 | WA | BuildingCode | 230 | 196 | 120 | CS Audience Seating Area - Exercise Center_2021WABuildingCode | CS Audience Seating Area - Exercise Center_2021WABuildingCodeScheduleSet | 6.6667 | 150 | 1.6146 | 710 | 208.0891 | 1090 | 319.4607 | 527.5498 | 97 | 120 | 0.39444 | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement_Spectator areas | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement_Spectator areasCOMNET-REV9PeopleDef | NECB-B-Occupancy | CS Audience Seating Area - Exercise CenterActivity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement_Spectator areas |  |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement_Spectator areasVent | 0.67425 | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - Exercise CenterElectricalEquipDef | NECB-B-Electric-Equipment | 0.23 | 2.4757 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Audience/seating area - Permanent - Otherwise | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - OtherwiseLightingDef | NECB-B-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Gym - audience | PNNL-NECB 2011DOE_PrototypeSpace Function_Gym - audienceInfil | Always On | Space Function | Gym - audience |  | 1.03 |  | Smooth | 0.01 | 50 | 332 | 863 | 0.9 | 0.65 | 0.65 | Mixed_AudienceSeating_ExCtr_10mm | CalculatedEstimate | RetractableAluminumBleacherSystem |  | Mixed_AudienceSeating_ExCtr_10mm | CalculatedEstimateRetractableAluminumBleacherSystemMixed_AudienceSeating_ExCtr_10mmInternalMassDef
CS Audience Seating Area - Gymnasium | 2021_WA_BuildingCode | Gymnasium | Audience Seating Area | Gym - audience | 2021 | WA | BuildingCode | 230 | 196 | 120 | CS Audience Seating Area - Gymnasium_2021WABuildingCode | CS Audience Seating Area - Gymnasium_2021WABuildingCodeScheduleSet | 6.6667 | 150 | 1.6146 | 710 | 208.0891 | 1090 | 319.4607 | 527.5498 | 97 | 120 | 0.39444 | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement_Spectator areas | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement_Spectator areasCOMNET-REV9PeopleDef | NECB-B-Occupancy | CS Audience Seating Area - GymnasiumActivity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement_Spectator areas |  |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement_Spectator areasVent | 0.67425 | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - GymnasiumElectricalEquipDef | NECB-B-Electric-Equipment | 0.23 | 2.4757 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Audience/seating area - Permanent - In a gymnasium | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - In a gymnasiumLightingDef | NECB-B-Lighting | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | SecondarySchool_Gym | PNNL-90.1-2013DOE_PrototypeSecondarySchool_GymInfil | SchoolSecondary INFIL_SCH_PNNL | SecondarySchool | Gym |  | 0.71 |  | Smooth | 0.01 | 50 | 382 | 851 | 0.9 | 0.65 | 0.65 | Mixed_AudienceSeating_Gymnasium_10mm | CalculatedEstimate | TelescopingAluminumBleacherSystem |  | Mixed_AudienceSeating_Gymnasium_10mm | CalculatedEstimateTelescopingAluminumBleacherSystemMixed_AudienceSeating_Gymnasium_10mmInternalMassDef
CS Audience Seating Area - Motion Picture Theater | 2021_WA_BuildingCode | Theater | Audience Seating Area | Audience - motion picture | 2021 | WA | BuildingCode | 230 | 196 | 120 | CS Audience Seating Area - Motion Picture Theater_2021WABuildingCode | CS Audience Seating Area - Motion Picture Theater_2021WABuildingCodeScheduleSet | 6.6667 | 150 | 1.6146 | 225 | 65.9437 | 105 | 30.7737 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Auditoriums | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsCOMNET-REV9PeopleDef | NECB-C-Occupancy | CS Audience Seating Area - Motion Picture TheaterActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Auditoriums |  |  | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsVent | 0.74485 | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - Motion Picture TheaterElectricalEquipDef | NECB-C-Electric-Equipment | 0.27 | 2.9063 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Audience/seating area - Permanent - In a motion picture theater | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - In a motion picture theaterLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Audience - motion picture | PNNL-NECB 2011DOE_PrototypeSpace Function_Audience - motion pictureInfil | Always On | Space Function | Audience - motion picture |  | 1.81 |  | MediumRough | 0.0341 | 0.891 | 210 | 876 | 0.9 | 0.65 | 0.65 | Mixed_AudienceSeating_MotionPictureTheater_34mm | CalculatedEstimate | FixedCinemaSeatsWithCupHolders |  | Mixed_AudienceSeating_MotionPictureTheater_34mm | CalculatedEstimateFixedCinemaSeatsWithCupHoldersMixed_AudienceSeating_MotionPictureTheater_34mmInternalMassDef
CS Audience Seating Area - Penitentiary | 2021_WA_BuildingCode | Penitentiary | Audience Seating Area | Penitentiary - audience | 2021 | WA | BuildingCode | 230 | 196 | 120 | CS Audience Seating Area - Penitentiary_2021WABuildingCode | CS Audience Seating Area - Penitentiary_2021WABuildingCodeScheduleSet | 20 | 50 | 0.5382 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Correctional facilities_Booking_waiting | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Correctional facilities_Booking_waitingCOMNET-REV9PeopleDef | NECB-C-Occupancy | CS Audience Seating Area - PenitentiaryActivity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Correctional facilities_Booking_waiting |  |  | Washington State Mechanical Code TABLE 403.3.1.1Correctional facilities_Booking_waitingVent | 0.74761 | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - PenitentiaryElectricalEquipDef | NECB-C-Electric-Equipment | 0.67 | 7.2119 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Audience/seating area - Permanent - In a penitentiary | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - In a penitentiaryLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Penitentiary - audience | PNNL-NECB 2011DOE_PrototypeSpace Function_Penitentiary - audienceInfil | Always On | Space Function | Penitentiary - audience |  | 1.17 |  | MediumSmooth | 0.0013 | 50 | 7800 | 460 | 0.9 | 0.7 | 0.7 | Steel_AudienceSeating_Penitentiary_1mm | CalculatedEstimate | FixedAllMetalSecuritySeating |  | Steel_AudienceSeating_Penitentiary_1mm | CalculatedEstimateFixedAllMetalSecuritySeatingSteel_AudienceSeating_Penitentiary_1mmInternalMassDef
CS Audience Seating Area - Performing Arts Theater | 2021_WA_BuildingCode | Theater | Audience Seating Area | Audience - performance arts | 2021 | WA | BuildingCode | 230 | 196 | 120 | CS Audience Seating Area - Performing Arts Theater_2021WABuildingCode | CS Audience Seating Area - Performing Arts Theater_2021WABuildingCodeScheduleSet | 6.6667 | 150 | 1.6146 | 225 | 65.9437 | 105 | 30.7737 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Auditoriums | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsCOMNET-REV9PeopleDef | NECB-C-Occupancy | CS Audience Seating Area - Performing Arts TheaterActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Auditoriums |  |  | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsVent | 0.74485 | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - Performing Arts TheaterElectricalEquipDef | NECB-C-Electric-Equipment | 1.16 | 12.4862 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Audience/seating area - Permanent - In a performing arts theater | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - In a performing arts theaterLightingDef | NECB-C-Lighting | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | SecondarySchool_Auditorium | PNNL-90.1-2013DOE_PrototypeSecondarySchool_AuditoriumInfil | SchoolSecondary INFIL_SCH_PNNL | SecondarySchool | Auditorium |  | 2.06 |  | MediumRough | 0.0379 | 0.863 | 200 | 879 | 0.9 | 0.65 | 0.65 | Mixed_AudienceSeating_PerformingArtsTheater_38mm | CalculatedEstimate | FixedUpholsteredSeatsWithAisleRails |  | Mixed_AudienceSeating_PerformingArtsTheater_38mm | CalculatedEstimateFixedUpholsteredSeatsWithAisleRailsMixed_AudienceSeating_PerformingArtsTheater_38mmInternalMassDef
CS Audience Seating Area - Religious Building | 2021_WA_BuildingCode | Religious | Audience Seating Area | Religious - audience | 2021 | WA | BuildingCode | 230 | 196 | 120 | CS Audience Seating Area - Religious Building_2021WABuildingCode | CS Audience Seating Area - Religious Building_2021WABuildingCodeScheduleSet | 6.6667 | 150 | 1.6146 | 245 | 71.8054 | 155 | 45.4279 | 117.2333 | 97 | 120 | 0.6125 | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Auditoriums | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsCOMNET-REV9PeopleDef | NECB-I-Occupancy | CS Audience Seating Area - Religious BuildingActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Auditoriums |  |  | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsVent | 0.73324 | 7.8926 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - Religious BuildingElectricalEquipDef | NECB-I-Electric-Equipment | 0.72 | 7.7501 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Audience/seating area - Permanent - In a religious building | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - In a religious buildingLightingDef | NECB-I-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Religious - audience | PNNL-NECB 2011DOE_PrototypeSpace Function_Religious - audienceInfil | Always On | Space Function | Religious - audience |  | 1.17 |  | MediumRough | 0.0182 | 1.185 | 255 | 785 | 0.9 | 0.7 | 0.7 | Mixed_AudienceSeating_ReligiousBuilding_18mm | CalculatedEstimate | PaddedStackableGangedChairs |  | Mixed_AudienceSeating_ReligiousBuilding_18mm | CalculatedEstimatePaddedStackableGangedChairsMixed_AudienceSeating_ReligiousBuilding_18mmInternalMassDef
CS Audience Seating Area - Sports Arena | 2021_WA_BuildingCode | Sports arena | Audience Seating Area | Sports arena - audience | 2021 | WA | BuildingCode | 230 | 196 | 120 | CS Audience Seating Area - Sports Arena_2021WABuildingCode | CS Audience Seating Area - Sports Arena_2021WABuildingCodeScheduleSet | 6.6667 | 150 | 1.6146 | 245 | 71.8054 | 105 | 30.7737 | 102.5791 | 97 | 120 | 0.7 | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement_Spectator areas | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement_Spectator areasCOMNET-REV9PeopleDef | NECB-B-Occupancy | CS Audience Seating Area - Sports ArenaActivity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement_Spectator areas |  |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement_Spectator areasVent | 0.74485 | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - Sports ArenaElectricalEquipDef | NECB-B-Electric-Equipment | 0.33 | 3.5521 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Audience/seating area - Permanent - In a sports arena | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - In a sports arenaLightingDef | NECB-B-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Sports arena - audience | PNNL-NECB 2011DOE_PrototypeSpace Function_Sports arena - audienceInfil | Always On | Space Function | Sports arena - audience |  | 1.75 |  | MediumSmooth | 0.01 | 2.66 | 440 | 1401 | 0.9 | 0.65 | 0.65 | Mixed_AudienceSeating_SportsArena_10mm | CalculatedEstimate | FoldDownPolypropyleneStadiumSeats |  | Mixed_AudienceSeating_SportsArena_10mm | CalculatedEstimateFoldDownPolypropyleneStadiumSeatsMixed_AudienceSeating_SportsArena_10mmInternalMassDef
CS Audience Seating Area - Transportation Facility | 2021_WA_BuildingCode | Transportation Facility | Audience Seating Area | Transp. seating | 2021 | WA | BuildingCode | 230 | 196 | 120 | CS Audience Seating Area - Transportation Facility_2021WABuildingCode | CS Audience Seating Area - Transportation Facility_2021WABuildingCodeScheduleSet | 10 | 100 | 1.0764 | 225 | 65.9437 | 105 | 30.7737 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1 | Transportation_Transportation waiting | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Transportation_Transportation waitingCOMNET-REV9PeopleDef | NECB-H-Occupancy | CS Audience Seating Area - Transportation FacilityActivity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Transportation_Transportation waiting |  |  | Washington State Mechanical Code TABLE 403.3.1.1Transportation_Transportation waitingVent | 0.74761 | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - Transportation FacilityElectricalEquipDef | NECB-H-Electric-Equipment | 0.23 | 2.4757 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Audience/seating area - Permanent - Otherwise | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - OtherwiseLightingDef | NECB-H-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2012 | DOE_Prototype | Space Function_Transp. seating | PNNL-NECB 2012DOE_PrototypeSpace Function_Transp. seatingInfil | Always On | Space Function | Transp. seating |  | 0.66 |  | MediumRough | 0.01 | 3.06 | 638 | 658 | 0.9 | 0.6 | 0.6 | Mixed_AudienceSeating_Transportation_10mm | CalculatedEstimate | GangedModularWaitingSeats |  | Mixed_AudienceSeating_Transportation_10mm | CalculatedEstimateGangedModularWaitingSeatsMixed_AudienceSeating_Transportation_10mmInternalMassDef
CS Audience Seating Area - Other | 2021_WA_BuildingCode | Miscellaneous | Audience Seating Area | Audience - auditorium | 2021 | WA | BuildingCode | 230 | 196 | 120 | CS Audience Seating Area - Other_2021WABuildingCode | CS Audience Seating Area - Other_2021WABuildingCodeScheduleSet | 10 | 100 | 1.0764 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Multiuse assembly | COMNET-REV9 | BA School/University | Washington State Mechanical Code TABLE 403.3.1.1Education_Multiuse assemblyCOMNET-REV9BA School/UniversityPeopleDef | NECB-C-Occupancy | CS Audience Seating Area - OtherActivity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Multiuse assembly |  |  | Washington State Mechanical Code TABLE 403.3.1.1Education_Multiuse assemblyVent | 0.74761 | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - OtherElectricalEquipDef | NECB-C-Electric-Equipment | 0.23 | 2.4757 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Audience/seating area - Permanent - Otherwise | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - OtherwiseLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2013 | DOE_Prototype | Space Function_Audience - auditorium | PNNL-NECB 2013DOE_PrototypeSpace Function_Audience - auditoriumInfil | Always On | Space Function | Audience - auditorium |  | 1.13 |  | MediumRough | 0.0079 | 1.86 | 364 | 691 | 0.9 | 0.65 | 0.65 | Mixed_AudienceSeating_Other_8mm | CalculatedEstimate | PortablePaddedFoldingChairs |  | Mixed_AudienceSeating_Other_8mm | CalculatedEstimatePortablePaddedFoldingChairsMixed_AudienceSeating_Other_8mmInternalMassDef
CS Atrium - Less than or equal to 40 ft | 2021_WA_BuildingCode | Atrium | Atrium - Less than or equal to 40 ft | Atrium | 2021 | WA | BuildingCode | 255 | 255 | 0 | CS Atrium - Less than or equal to 40 ft_2021WABuildingCode | CS Atrium - Less than or equal to 40 ft_2021WABuildingCodeScheduleSet | [20 empty] | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces_Corridors other than Group R |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_Corridors other than Group RVent | [10 empty] | 0.48 | 5.1667 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Atrium - 20 to 40 feet in height | Washington State Energy Code Commercial TABLE C405.4.2Atrium - 20 to 40 feet in heightLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2014 | DOE_Prototype | Space Function_Atrium - H < 13m | PNNL-NECB 2014DOE_PrototypeSpace Function_Atrium - H < 13mInfil | Always On | Space Function | Atrium - H < 13m |  | 0.31 |  | MediumRough | 0.085 | 2.56 | 904 | 1122 | 0.9 | 0.7 | 0.7 | Mixed_Atrium_LTE40ft_85mm | CalculatedEstimate | LightWoodTrussesOrSmallSteelBeams |  | Mixed_Atrium_LTE40ft_85mm | CalculatedEstimateLightWoodTrussesOrSmallSteelBeamsMixed_Atrium_LTE40ft_85mmInternalMassDef
CS Atrium - More than 40 ft | 2021_WA_BuildingCode | Atrium | Atrium - More than 40 ft | Atrium | 2021 | WA | BuildingCode | 255 | 255 | 0 | CS Atrium - More than 40 ft_2021WABuildingCode | CS Atrium - More than 40 ft_2021WABuildingCodeScheduleSet | [20 empty] | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces_Corridors other than Group R |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_Corridors other than Group RVent | [10 empty] | 0.6 | 6.4584 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Atrium - Above 40 feet in height | Washington State Energy Code Commercial TABLE C405.4.2Atrium - Above 40 feet in heightLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2015 | DOE_Prototype | Space Function_Atrium - H > 13m | PNNL-NECB 2015DOE_PrototypeSpace Function_Atrium - H > 13mInfil | Always On | Space Function | Atrium - H > 13m |  | 0.36 |  | MediumRough | 0.1294 | 3.01 | 886 | 1270 | 0.9 | 0.7 | 0.7 | Mixed_Atrium_GT40ft_129mm | CalculatedEstimate | HeavyGlulamBeamsOrSteelMembers |  | Mixed_Atrium_GT40ft_129mm | CalculatedEstimateHeavyGlulamBeamsOrSteelMembersMixed_Atrium_GT40ft_129mmInternalMassDef
CS Banking Activity Area | 2021_WA_BuildingCode | Bank | Banking Activity Area | Bank - banking and offices | 2021 | WA | BuildingCode | 204 | 255 | 229 | CS Banking Activity Area_2021WABuildingCode | CS Banking Activity Area_2021WABuildingCodeScheduleSet | 25 | 40 | 0.43056 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces_Museums/galleries | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_Museums/galleries COMNET-REV9PeopleDef | NECB-A-Occupancy | CS Banking Activity AreaActivity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces_Museums/galleries |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_Museums/galleries Vent | 1.7201 | 18.5149 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Banking Activity AreaElectricalEquipDef | NECB-A-Electric-Equipment | 0.61 | 6.566 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Banking activity area | Washington State Energy Code Commercial TABLE C405.4.2Banking activity areaLightingDef | NECB-A-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2016 | DOE_Prototype | Space Function_Bank - banking and offices | PNNL-NECB 2016DOE_PrototypeSpace Function_Bank - banking and officesInfil | Always On | Space Function | Bank - banking and offices |  | 0.69 |  | MediumRough | 0.0151 | 5.243 | 1547 | 811 | 0.9 | 0.7 | 0.7 | Mixed_Banking_ActivityArea_15mm | CalculatedEstimate | TellerCountersAndSecurityTransactionWindows |  | Mixed_Banking_ActivityArea_15mm | CalculatedEstimateTellerCountersAndSecurityTransactionWindowsMixed_Banking_ActivityArea_15mmInternalMassDef
CS Classroom/Lecture/Training - Penitentiary | 2021_WA_BuildingCode | Penitentiary | Classroom/Lecture/Training | Penitentiary - classroom | 2021 | WA | BuildingCode | 204 | 120 | 230 | CS Classroom/Lecture/Training - Penitentiary_2021WABuildingCode | CS Classroom/Lecture/Training - Penitentiary_2021WABuildingCodeScheduleSet | 15.3846 | 65 | 0.69965 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Lecture classroom | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Education_Lecture classroom COMNET-REV9PeopleDef | NECB-D-Occupancy | CS Classroom/Lecture/Training - PenitentiaryActivity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Lecture classroom |  |  | Washington State Mechanical Code TABLE 403.3.1.1Education_Lecture classroom Vent | 0.58913 | 6.3414 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Classroom/Lecture/Training - PenitentiaryElectricalEquipDef | NECB-D-Electric-Equipment | 0.89 | 9.58 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Classroom/lecture hall/training room - In a penitentiary | Washington State Energy Code Commercial TABLE C405.4.2Classroom/lecture hall/training room - In a penitentiaryLightingDef | NECB-D-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Classroom/lecture/training | PNNL-NECB 2011DOE_PrototypeSpace Function_Classroom/lecture/trainingInfil | Always On | Space Function | Classroom/lecture/training |  | 0.85 |  | MediumSmooth | 0.0043 | 9.44 | 1923 | 895 | 0.9 | 0.55 | 0.5 | Mixed_Classroom_Penitentiary_4mm | CalculatedEstimate | LaminateDeskSteelChairInstitutional |  | Mixed_Classroom_Penitentiary_4mm | CalculatedEstimateLaminateDeskSteelChairInstitutionalMixed_Classroom_Penitentiary_4mmInternalMassDef
CS Classroom/Lecture/Training - K-12 - laboratory and shops | 2021_WA_BuildingCode | Secondary School | Classroom/Lecture/Training - K-12 - laboratory and shops | SecondarySchool Classroom | 2021 | WA | BuildingCode | 204 | 120 | 230 | CS Classroom/Lecture/Training - K-12 - laboratory and shops_2021WABuildingCode | CS Classroom/Lecture/Training - K-12 - laboratory and shops_2021WABuildingCodeScheduleSet | 15.3846 | 65 | 0.69965 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Lecture classroom | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Education_Lecture classroom COMNET-REV9PeopleDef | SchoolSecondary BLDG_OCC_SCH_Gym | CS Classroom/Lecture/Training - K-12 - laboratory and shopsActivity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Lecture classroom |  |  | Washington State Mechanical Code TABLE 403.3.1.1Education_Lecture classroom Vent | 0.58913 | 6.3414 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Classroom/Lecture/Training - K-12 - laboratory and shopsElectricalEquipDef | SchoolSecondary BLDG_EQUIP_SCH | 1.11 | 11.948 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Laboratory - In or as a classrooms | Washington State Energy Code Commercial TABLE C405.4.2Laboratory - In or as a classroomsLightingDef | SchoolSecondary BLDG_LIGHT_GYM_SCH | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | SecondarySchool_Classroom | PNNL-90.1-2013DOE_PrototypeSecondarySchool_ClassroomInfil | Always On | SecondarySchool | Classroom |  | 2.35 |  | MediumRough | 0.00428 | 14 | 2572 | 659 | 0.9 | 0.7 | 0.7 | Mixed_ClassroomK12_LabShop_4mm | CalculatedEstimate | SteelBenchesCaseworkAndShopMachines |  | Mixed_ClassroomK12_LabShop_4mm | CalculatedEstimateSteelBenchesCaseworkAndShopMachinesMixed_ClassroomK12_LabShop_4mmInternalMassDef
CS Classroom/Lecture/Training - Other | 2021_WA_BuildingCode | School/University | Classroom/Lecture/Training | Classroom/lecture/training | 2021 | WA | BuildingCode | 204 | 120 | 230 | CS Classroom/Lecture/Training - Other_2021WABuildingCode | CS Classroom/Lecture/Training - Other_2021WABuildingCodeScheduleSet | 15.3846 | 65 | 0.69965 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Lecture classroom | COMNET-REV9 | BA School/University | Washington State Mechanical Code TABLE 403.3.1.1Education_Lecture classroom COMNET-REV9BA School/UniversityPeopleDef | NECB-D-Occupancy | CS Classroom/Lecture/Training - OtherActivity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Education_Lecture classroom |  |  | Washington State Mechanical Code TABLE 403.3.1.1Education_Lecture classroom Vent | 0.58913 | 6.3414 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Classroom/Lecture/Training - OtherElectricalEquipDef | NECB-D-Electric-Equipment | 0.71 | 7.6424 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Classroom/lecture hall/training room - Otherwise | Washington State Energy Code Commercial TABLE C405.4.2Classroom/lecture hall/training room - OtherwiseLightingDef | NECB-D-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Classroom/lecture/training | PNNL-NECB 2011DOE_PrototypeSpace Function_Classroom/lecture/trainingInfil | Always On | Space Function | Classroom/lecture/training |  | 1.3 |  | MediumRough | 0.0078 | 2.85 | 894 | 936 | 0.9 | 0.6 | 0.6 | Mixed_ClassroomTraining_Other_8mm | CalculatedEstimate | MovableLaminateTablesAndStackingChairs |  | Mixed_ClassroomTraining_Other_8mm | CalculatedEstimateMovableLaminateTablesAndStackingChairsMixed_ClassroomTraining_Other_8mmInternalMassDef
CS Conference/Meeting/Multipurpose | 2021_WA_BuildingCode | Office | Conference/Meeting/Multipurpose | Office Conference | 2021 | WA | BuildingCode | 230 | 196 | 120 | CS Conference/Meeting/Multipurpose_2021WABuildingCode | CS Conference/Meeting/Multipurpose_2021WABuildingCodeScheduleSet | 20 | 50 | 0.5382 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Office_Conference rooms | COMNET-REV9 | BA Office | Washington State Mechanical Code TABLE 403.3.1.1Office_Conference roomsCOMNET-REV9BA OfficePeopleDef | OfficeMedium BLDG_OCC_SCH | CS Conference/Meeting/MultipurposeActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Office_Conference rooms |  |  | Washington State Mechanical Code TABLE 403.3.1.1Office_Conference roomsVent | 0.73324 | 7.8926 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Conference/Meeting/MultipurposeElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 0.97 | 10.4411 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Conference/meeting/multipurpose | Washington State Energy Code Commercial TABLE C405.4.2Conference/meeting/multipurposeLightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Conf./meet./multi-purpose | PNNL-NECB 2011DOE_PrototypeSpace Function_Conf./meet./multi-purposeInfil | Always On | Space Function | Conf./meet./multi-purpose |  | 0.61 |  | MediumRough | 0.0059 | 42.8 | 1804 | 1243 | 0.9 | 0.7 | 0.65 | Conference_Meeting_Multipurpose_Material | CalculatedEstimate | ConferenceTablesChairsAndCredenza |  | Conference_Meeting_Multipurpose_Material | CalculatedEstimateConferenceTablesChairsAndCredenzaConference_Meeting_Multipurpose_MaterialInternalMassDef
CS Confinment Cells | 2021_WA_BuildingCode | Courthouse | Confinment Cells | Courthouse - cell | 2021 | WA | BuildingCode | 192 | 192 | 192 | CS Confinment Cells_2021WABuildingCode | CS Confinment Cells_2021WABuildingCodeScheduleSet | 40 | 25 | 0.2691 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Correctional facilities_Cells With plumbing fixtures | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Correctional facilities_Cells With plumbing fixturesCOMNET-REV9BA OfficePeopleDef | NECB-H-Occupancy | CS Confinment CellsActivity | 5 | 0.0023596 | 0.12 | 0.0006096 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Correctional facilities_Cells With plumbing fixtures |  |  | Washington State Mechanical Code TABLE 403.3.1.1Correctional facilities_Cells With plumbing fixturesVent | 1.4928 | 16.0688 | 0 | 0.5 | 0 | COMNET-REV9 | NREL 956/Eley Analysis | DOEPrototype | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Confinment CellsElectricalEquipDef | NECB-H-Electric-Equipment | 0.7 | 7.5348 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Confinement cell | Washington State Energy Code Commercial TABLE C405.4.2Confinement cellLightingDef | NECB-H-Lighting | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Office_Conference | PNNL-90.1-2013DOE_PrototypeOffice_ConferenceInfil | OfficeMedium INFIL_SCH_PNNL | Office | Conference |  | 0.73 |  | Smooth | 0.0043 | 33.8 | 7746 | 492 | 0.9 | 0.7 | 0.7 | Steel_Security_Fixtures_4mm | CalculatedEstimate | FixedSteelBedDeskAndToiletFixtures |  | Steel_Security_Fixtures_4mm | CalculatedEstimateFixedSteelBedDeskAndToiletFixturesSteel_Security_Fixtures_4mmInternalMassDef
CS Copy/Print Room | 2021_WA_BuildingCode | Office | Copy/Print Room | PrintRoom | 2021 | WA | BuildingCode | 41 | 31 | 169 | CS Copy/Print Room_2021WABuildingCode | CS Copy/Print Room_2021WABuildingCodeScheduleSet | 250 | 4 | 0.043056 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Workrooms_Copy_printing rooms | COMNET-REV9 | BA Office | Washington State Mechanical Code TABLE 403.3.1.1Workrooms_Copy_printing rooms COMNET-REV9BA OfficePeopleDef | OfficeMedium BLDG_OCC_SCH | CS Copy/Print RoomActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Workrooms_Copy_printing rooms |  |  | Washington State Mechanical Code TABLE 403.3.1.1Workrooms_Copy_printing rooms Vent | 1.6721 | 17.9987 | 0 | 0.5 | 0 | COMNET-REV9 | BA Office | WholeBuilding | COMNET-REV9BA OfficeWholeBuildingCS Copy/Print RoomElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 0.31 | 3.3368 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Copy/print room | Washington State Energy Code Commercial TABLE C405.4.2Copy/print roomLightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Office_PrintRoom | PNNL-90.1-2013DOE_PrototypeOffice_PrintRoomInfil | OfficeMedium INFIL_SCH_PNNL | Office | PrintRoom |  | 1.52 |  | MediumRough | 0.0015 | 39.6 | 6545 | 629 | 0.9 | 0.7 | 0.65 | Steel_Office_Equipment_2mm | CalculatedEstimate | CommercialCopierAndSteelStorageCabinets |  | Steel_Office_Equipment_2mm | CalculatedEstimateCommercialCopierAndSteelStorageCabinetsSteel_Office_Equipment_2mmInternalMassDef
CS Corridor - Assisted Living | 2021_WA_BuildingCode | Assisted Living | Corridor | Office Corridor | 2021 | WA | BuildingCode | 169 | 31 | 31 | CS Corridor - Assisted Living_2021WABuildingCode | CS Corridor - Assisted Living_2021WABuildingCodeScheduleSet | [20 empty] | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces_Corridors serving Group R |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_Corridors serving Group R Vent | 1.4046 | 15.1196 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Corridor - Assisted LivingElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 0.71 | 7.6424 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Corridor - In a facility for the visually impaired (and not used primarily by the staff) | Washington State Energy Code Commercial TABLE C405.4.2Corridor - In a facility for the visually impaired (and not used primarily by the staff)LightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | MidriseApartment_Corridor | PNNL-90.1-2013DOE_PrototypeMidriseApartment_CorridorInfil | ApartmentMidRise INF_APT_SCH | MidriseApartment | Corridor |  | 0.19 |  | Smooth | 0.0027 | 182.5 | 3009 | 894 | 0.9 | 0.7 | 0.7 | Aluminum_Corridor_Fixtures_3mm | CalculatedEstimate | AluminumHandrailsAndWayfindingSignage |  | Aluminum_Corridor_Fixtures_3mm | CalculatedEstimateAluminumHandrailsAndWayfindingSignageAluminum_Corridor_Fixtures_3mmInternalMassDef
CS Corridor - Hospital | 2021_WA_BuildingCode | Hospital | Corridor | Hospital Corridor | 2021 | WA | BuildingCode | 169 | 31 | 31 | CS Corridor - Hospital_2021WABuildingCode | CS Corridor - Hospital_2021WABuildingCodeScheduleSet | [20 empty] | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces_Corridors other than Group R |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_Corridors other than Group RVent | 1.2488 | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Corridor - HospitalElectricalEquipDef | Hospital BLDG_EQUIP_SCH | 0.71 | 7.6424 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Corridor - In a hospital | Washington State Energy Code Commercial TABLE C405.4.2Corridor - In a hospitalLightingDef | Hospital BLDG_LIGHT_CORRIDOR_SCH | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Hospital_Corridor | PNNL-90.1-2013DOE_PrototypeHospital_CorridorInfil | Hospital INFIL_SCH_PNNL | Hospital | Corridor |  | 0.26 |  | Smooth | 0.0025 | 64.8 | 6330 | 644 | 0.9 | 0.7 | 0.7 | Stainless_Aluminum_Hospital_3mm | CalculatedEstimate | StainlessHandrailsAndMedicalSignage |  | Stainless_Aluminum_Hospital_3mm | CalculatedEstimateStainlessHandrailsAndMedicalSignageStainless_Aluminum_Hospital_3mmInternalMassDef
CS Corridor - Manufacturing | 2021_WA_BuildingCode | Manufacturing Facility | Corridor | Mfg - corr. >= 2.4m | 2021 | WA | BuildingCode | 169 | 31 | 31 | CS Corridor - Manufacturing_2021WABuildingCode | CS Corridor - Manufacturing_2021WABuildingCodeScheduleSet | 143 | 6.993 | 0.075272 | 580 | 169.9883 | 870 | 254.9824 | 424.9707 | 97 | 120 | 0.4 | COMNET-REV9 |  |  |  | COMNET-REV9CS Corridor - ManufacturingPeopleDef | NECB-A-Occupancy | CS Corridor - ManufacturingActivity |  |  | 0.25 | 0.00127 |  |  |  | COMNET-REV9 |  |  |  | COMNET-REV9CS Corridor - ManufacturingVent | 0.34481 | 3.7116 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Corridor - ManufacturingElectricalEquipDef | NECB-A-Electric-Equipment | 0.41 | 4.4132 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Corridor - In a manufacturing facility | Washington State Energy Code Commercial TABLE C405.4.2Corridor - In a manufacturing facilityLightingDef | NECB-A-Lighting | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Office_Corridor | PNNL-90.1-2013DOE_PrototypeOffice_CorridorInfil | OfficeMedium INFIL_SCH_PNNL | Office | Corridor |  | 0.34 |  | MediumRough | 0.0063 | 82 | 5095 | 711 | 0.9 | 0.7 | 0.7 | Steel_Aluminum_Industrial_6mm | CalculatedEstimate | SteelHandrailsAndSafetyBollards |  | Steel_Aluminum_Industrial_6mm | CalculatedEstimateSteelHandrailsAndSafetyBollardsSteel_Aluminum_Industrial_6mmInternalMassDef
CS Corridor - Other | 2021_WA_BuildingCode | Miscellaneous | Corridor | SecondarySchool Corridor | 2021 | WA | BuildingCode | 169 | 31 | 31 | CS Corridor - Other_2021WABuildingCode | CS Corridor - Other_2021WABuildingCodeScheduleSet | [20 empty] | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces_Corridors other than Group R |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_Corridors other than Group RVent | 0.3 | 3.2292 | 0 | 0.5 | 0 | COMNET-REV9 | BA Warehouse | WholeBuilding | COMNET-REV9BA WarehouseWholeBuildingCS Corridor - OtherElectricalEquipDef | SchoolSecondary BLDG_EQUIP_SCH | 0.41 | 4.4132 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Corridor - Otherwise | Washington State Energy Code Commercial TABLE C405.4.2Corridor - OtherwiseLightingDef | SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | [11 empty] | 0.019242 |  | 9.081e-06 | PNNL- | 90.1-2013 | DOE_Prototype | LargeHotel_Corridor | PNNL-90.1-2013DOE_PrototypeLargeHotel_CorridorInfil | HotelLarge INFIL_QUARTER_ON_SCH | LargeHotel | Corridor |  | 0.19 |  | Smooth | 0.0027 | 186.9 | 2928 | 898 | 0.9 | 0.7 | 0.7 | Aluminum_Commercial_Fixtures_3mm | CalculatedEstimate | AluminumHandrailsAndDirectionalSignage |  | Aluminum_Commercial_Fixtures_3mm | CalculatedEstimateAluminumHandrailsAndDirectionalSignageAluminum_Commercial_Fixtures_3mmInternalMassDef
CS Courtroom | 2021_WA_BuildingCode | Courthouse | Courtroom | Courthouse - courtroom | 2021 | WA | BuildingCode | 153 | 76 | 0 | CS Courtroom_2021WABuildingCode | CS Courtroom_2021WABuildingCodeScheduleSet | 14.2857 | 70 | 0.75347 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces_Courtrooms | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_CourtroomsCOMNET-REV9PeopleDef | NECB-A-Occupancy | CS CourtroomActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces_Courtrooms |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_CourtroomsVent | 1.4928 | 16.0688 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS CourtroomElectricalEquipDef | NECB-A-Electric-Equipment | 1.2 | 12.9168 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Courtroom | Washington State Energy Code Commercial TABLE C405.4.2CourtroomLightingDef | NECB-A-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Courthouse - courtroom | PNNL-NECB 2011DOE_PrototypeSpace Function_Courthouse - courtroomInfil | Always On | Space Function | Courthouse - courtroom |  | 0.84 |  | MediumRough | 0.024 | 3.54 | 596 | 1580 | 0.9 | 0.7 | 0.65 | Wood_Courtroom_Furniture_24mm | CalculatedEstimate | SolidHardwoodBenchesAndGallerySeating |  | Wood_Courtroom_Furniture_24mm | CalculatedEstimateSolidHardwoodBenchesAndGallerySeatingWood_Courtroom_Furniture_24mmInternalMassDef
CS Computer Room | 2021_WA_BuildingCode | Office | Computer Room | Office IT_Room | 2021 | WA | BuildingCode | 41 | 31 | 169 | CS Computer Room_2021WABuildingCode | CS Computer Room_2021WABuildingCodeScheduleSet | 250 | 4 | 0.043056 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Workrooms_Computer without printing | COMNET-REV9 | BA Office | Washington State Mechanical Code TABLE 403.3.1.1Workrooms_Computer without printingCOMNET-REV9BA OfficePeopleDef | OfficeMedium BLDG_OCC_SCH | CS Computer RoomActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Workrooms_Computer without printing |  |  | Washington State Mechanical Code TABLE 403.3.1.1Workrooms_Computer without printingVent | 60 | 645.84 | 0 | 0.5 | 0 | Estimate |  | DOEPrototype | EstimateDOEPrototypeCS Computer RoomElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 0.94 | 10.1182 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Computer room, data center | Washington State Energy Code Commercial TABLE C405.4.2Computer room, data centerLightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Office_IT_Room | PNNL-90.1-2013DOE_PrototypeOffice_IT_RoomInfil | OfficeMedium INFIL_SCH_PNNL | Office | IT_Room |  | 1.62 |  | MediumRough | 0.0022 | 59 | 4439 | 844 | 0.9 | 0.7 | 0.65 | Steel_IT_Equipment_2mm | CalculatedEstimate | ITWorkstationsAndServerRack |  | Steel_IT_Equipment_2mm | CalculatedEstimateITWorkstationsAndServerRackSteel_IT_Equipment_2mmInternalMassDef
CS Dining Area - Penitentiary | 2021_WA_BuildingCode | Penitentiary | Dining Area | Penitentiary - dining | 2021 | WA | BuildingCode | 31 | 169 | 34 | CS Dining Area - Penitentiary_2021WABuildingCode | CS Dining Area - Penitentiary_2021WABuildingCodeScheduleSet | 14.2857 | 70 | 0.75347 | 275 | 80.5979 | 275 | 80.5979 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1 | Food and beverage service_Dining rooms | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Dining roomsCOMNET-REV9PeopleDef | NECB-B-Occupancy | CS Dining Area - PenitentiaryActivity | 7.5 | 0.0035394 | 0.18 | 0.0009144 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Food and beverage service_Dining rooms |  |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Dining roomsVent | 1.263 | 13.5949 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Dining Area - PenitentiaryElectricalEquipDef | NECB-B-Electric-Equipment | 0.42 | 4.5209 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Dining area - In a penitentiary | Washington State Energy Code Commercial TABLE C405.4.2Dining area - In a penitentiaryLightingDef | NECB-B-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Penitentiary - dining | PNNL-NECB 2011DOE_PrototypeSpace Function_Penitentiary - diningInfil | Always On | Space Function | Penitentiary - dining |  | 0.74 |  | Smooth | 0.0027 | 42.6 | 7746 | 478 | 0.9 | 0.7 | 0.7 | Steel_Security_Dining_3mm | CalculatedEstimate | FixedSteelTableBenchUnits |  | Steel_Security_Dining_3mm | CalculatedEstimateFixedSteelTableBenchUnitsSteel_Security_Dining_3mmInternalMassDef
CS Dining Area - Assisted Living | 2021_WA_BuildingCode | Hotel/Motel | Dining Area | Hotel/Motel - dining | 2021 | WA | BuildingCode | 31 | 169 | 34 | CS Dining Area - Assisted Living_2021WABuildingCode | CS Dining Area - Assisted Living_2021WABuildingCodeScheduleSet | 14.2857 | 70 | 0.75347 | 275 | 80.5979 | 275 | 80.5979 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1 | Food and beverage service_Dining rooms | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Dining roomsCOMNET-REV9PeopleDef | NECB-B-Occupancy | CS Dining Area - Assisted LivingActivity | 7.5 | 0.0035394 | 0.18 | 0.0009144 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Food and beverage service_Dining rooms |  |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Dining roomsVent | 1.3161 | 14.166 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Dining Area - Assisted LivingElectricalEquipDef | NECB-B-Electric-Equipment | 1.27 | 13.6703 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Dining area - In a facility for the visually impaired (and not used primarily by the staff) | Washington State Energy Code Commercial TABLE C405.4.2Dining area - In a facility for the visually impaired (and not used primarily by the staff)LightingDef | NECB-B-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Dining - family_WholeBuilding | PNNL-NECB 2011DOE_PrototypeDining - family_WholeBuildingInfil | Always On | Dining - family | WholeBuilding |  | 1.44 |  | MediumRough | 0.0074 | 6.95 | 877 | 1320 | 0.9 | 0.7 | 0.65 | Wood_Composite_Residential_7mm | CalculatedEstimate | ResidentialStyleDiningFurniture |  | Wood_Composite_Residential_7mm | CalculatedEstimateResidentialStyleDiningFurnitureWood_Composite_Residential_7mmInternalMassDef
CS Dining Area - Bar Lounge/Leisure | 2021_WA_BuildingCode | Bar/Lounge | Dining Area | Dining - bar lounge/leisure | 2021 | WA | BuildingCode | 31 | 169 | 34 | CS Dining Area - Bar Lounge/Leisure _2021WABuildingCode | CS Dining Area - Bar Lounge/Leisure _2021WABuildingCodeScheduleSet | 10 | 100 | 1.0764 | 275 | 80.5979 | 275 | 80.5979 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1 | Food and beverage service_Bars_cocktail lounges | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Bars_cocktail loungesCOMNET-REV9PeopleDef | NECB-B-Occupancy | CS Dining Area - Bar Lounge/Leisure Activity | 7.5 | 0.0035394 | 0.18 | 0.0009144 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Food and beverage service_Bars_cocktail lounges |  |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Bars_cocktail loungesVent | 1.263 | 13.5949 | 0.25 | 0.3 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Dining Area - Bar Lounge/Leisure ElectricalEquipDef | NECB-B-Electric-Equipment | 0.86 | 9.257 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Dining area - In a bar/lounge or leisure dining | Washington State Energy Code Commercial TABLE C405.4.2Dining area - In a bar/lounge or leisure diningLightingDef | NECB-B-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Dining - bar lounge/leisure | PNNL-NECB 2011DOE_PrototypeSpace Function_Dining - bar lounge/leisureInfil | Always On | Space Function | Dining - bar lounge/leisure |  | 1.79 |  | MediumRough | 0.0028 | 9.72 | 2241 | 1189 | 0.9 | 0.7 | 0.65 | Mixed_Commercial_BarLounge_3mm | CalculatedEstimate | BarCounterAndMixedSeating |  | Mixed_Commercial_BarLounge_3mm | CalculatedEstimateBarCounterAndMixedSeatingMixed_Commercial_BarLounge_3mmInternalMassDef
CS Dining Area - Cafeteria or Fast Food | 2021_WA_BuildingCode | Quick Service Restaurant | Dining Area | QuickServiceRestaurant Dining | 2021 | WA | BuildingCode | 31 | 169 | 34 | CS Dining Area - Cafeteria or Fast Food _2021WABuildingCode | CS Dining Area - Cafeteria or Fast Food _2021WABuildingCodeScheduleSet | 10 | 100 | 1.0764 | 275 | 80.5979 | 275 | 80.5979 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1 | Food and beverage service_Cafeteria_fast food | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Cafeteria_fast food COMNET-REV9PeopleDef | RestaurantFastFood BLDG_OCC_SCH | CS Dining Area - Cafeteria or Fast Food Activity | 7.5 | 0.0035394 | 0.18 | 0.0009144 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Food and beverage service_Cafeteria_fast food |  |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Cafeteria_fast food Vent | 1.3684 | 14.729 | 0.25 | 0.3 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Dining Area - Cafeteria or Fast Food ElectricalEquipDef | RestaurantFastFood BLDG_EQUIP_SCH | 0.4 | 4.3056 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Dining area - In cafeteria or fast food dining | Washington State Energy Code Commercial TABLE C405.4.2Dining area - In cafeteria or fast food diningLightingDef | RestaurantFastFood BLDG_LIGHT_DINING_SCH_2013 | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Dining - cafeteria_WholeBuilding | PNNL-NECB 2011DOE_PrototypeDining - cafeteria_WholeBuildingInfil | Always On | Dining - cafeteria | WholeBuilding |  | 1.68 |  | Smooth | 0.0027 | 19.2 | 2705 | 1099 | 0.9 | 0.7 | 0.65 | Laminate_Commercial_FastFood_3mm | CalculatedEstimate | FixedBoothAndMoldedChairs |  | Laminate_Commercial_FastFood_3mm | CalculatedEstimateFixedBoothAndMoldedChairsLaminate_Commercial_FastFood_3mmInternalMassDef
CS Dining Area - Family Dining | 2021_WA_BuildingCode | Restaurant | Dining Area | Dining - family space | 2021 | WA | BuildingCode | 31 | 169 | 34 | CS Dining Area - Family Dining _2021WABuildingCode | CS Dining Area - Family Dining _2021WABuildingCodeScheduleSet | 14.2857 | 70 | 0.75347 | 275 | 80.5979 | 275 | 80.5979 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1 | Food and beverage service_Dining rooms | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Dining roomsCOMNET-REV9PeopleDef | NECB-B-Occupancy | CS Dining Area - Family Dining Activity | 7.5 | 0.0035394 | 0.18 | 0.0009144 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Food and beverage service_Dining rooms |  |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Dining roomsVent | 1.3161 | 14.166 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Dining Area - Family Dining ElectricalEquipDef | NECB-B-Electric-Equipment | 0.6 | 6.4584 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Dining area - In a family dining area | Washington State Energy Code Commercial TABLE C405.4.2Dining area - In a family dining areaLightingDef | NECB-B-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Dining - family_WholeBuilding | PNNL-NECB 2011DOE_PrototypeDining - family_WholeBuildingInfil | Always On | Dining - family | WholeBuilding |  | 2.9 |  | MediumRough | 0.0055 | 4.74 | 802 | 1360 | 0.9 | 0.7 | 0.65 | Wood_Composite_Family_Dining_6mm | CalculatedEstimate | BoothSeatingAndUpholsteredChairs |  | Wood_Composite_Family_Dining_6mm | CalculatedEstimateBoothSeatingAndUpholsteredChairsWood_Composite_Family_Dining_6mmInternalMassDef
CS Dining Area - Other | 2021_WA_BuildingCode | Dining - other | Dining Area | Dining - other | 2021 | WA | BuildingCode | 31 | 169 | 34 | CS Dining Area - Other_2021WABuildingCode | CS Dining Area - Other_2021WABuildingCodeScheduleSet | 14.2857 | 70 | 0.75347 | 275 | 80.5979 | 275 | 80.5979 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1 | Food and beverage service_Dining rooms | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Dining roomsCOMNET-REV9PeopleDef | NECB-B-Occupancy | CS Dining Area - OtherActivity | 7.5 | 0.0035394 | 0.18 | 0.0009144 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Food and beverage service_Dining rooms |  |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Dining roomsVent | 1.3161 | 14.166 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Dining Area - OtherElectricalEquipDef | NECB-B-Electric-Equipment | 0.43 | 4.6285 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Dining area - Otherwise | Washington State Energy Code Commercial TABLE C405.4.2Dining area - OtherwiseLightingDef | NECB-B-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Dining - other | PNNL-NECB 2011DOE_PrototypeSpace Function_Dining - otherInfil | Always On | Space Function | Dining - other |  | 2.43 |  | MediumRough | 0.0028 | 5.29 | 1440 | 1288 | 0.9 | 0.7 | 0.65 | Mixed_Commercial_Dining_3mm | CalculatedEstimate | GenericBoothAndTableSeating |  | Mixed_Commercial_Dining_3mm | CalculatedEstimateGenericBoothAndTableSeatingMixed_Commercial_Dining_3mmInternalMassDef
CS Electrical/Mechanical | 2021_WA_BuildingCode | Elec/Mech Room | Electrical/Mechanical | Office Elec/MechRoom | 2021 | WA | BuildingCode | 41 | 31 | 175 | CS Electrical/Mechanical_2021WABuildingCode | CS Electrical/Mechanical_2021WABuildingCodeScheduleSet | [20 empty] | 0.12 | 0.0006096 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Retail stores, sales floors, and showroom floors - Storage rooms |  |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Storage roomsVent | 1.6721 | 17.9987 | 0 | 0.5 | 0 | COMNET-REV9 | BA Office | WholeBuilding | COMNET-REV9BA OfficeWholeBuildingCS Electrical/MechanicalElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 0.43 | 4.6285 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Electrical/mechanical | Washington State Energy Code Commercial TABLE C405.4.2Electrical/mechanicalLightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Electrical/Mechanical | PNNL-NECB 2011DOE_PrototypeSpace Function_Electrical/MechanicalInfil | Always On | Space Function | Electrical/Mechanical |  | 3.48 |  | Smooth | 0.0028 | 56.7 | 7047 | 511 | 0.9 | 0.7 | 0.7 | Steel_Mechanical_Equipment_3mm | CalculatedEstimate | HVACAndElectricalEquipment |  | Steel_Mechanical_Equipment_3mm | CalculatedEstimateHVACAndElectricalEquipmentSteel_Mechanical_Equipment_3mmInternalMassDef
CS Emergency Vehicle Garage | 2021_WA_BuildingCode | Parking Garage | Emergency Vehicle Garage | Parking garage space | 2021 | WA | BuildingCode | 153 | 0 | 76 | CS Emergency Vehicle Garage_2021WABuildingCode | CS Emergency Vehicle Garage_2021WABuildingCodeScheduleSet | [22 empty] | 0.75 | 0.00035396 |  | Washington State Mechanical Code TABLE 403.3.1.1 | Storage_Repair garages_enclosed parking garage |  |  | Washington State Mechanical Code TABLE 403.3.1.1Storage_Repair garages_enclosed parking garageVent | 0.57608 | 6.2009 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Emergency Vehicle GarageElectricalEquipDef | NECB-H-Electric-Equipment | 0.52 | 5.5973 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Emergency vehicle garage | Washington State Energy Code Commercial TABLE C405.4.2Emergency vehicle garageLightingDef | NECB-H-Lighting | [11 empty] | 0.2 |  | 9.4389e-05 | Estimate |  |  | Space Function_Parking garage space | EstimateSpace Function_Parking garage spaceInfil | Always On | Space Function | Parking garage space |  | 1.1 |  | MediumRough | 0.0017 | 45.8 | 7368 | 517 | 0.9 | 0.7 | 0.7 | Steel_Emergency_Garage_2mm | CalculatedEstimate | ApparatusBayStorageAndLockers |  | Steel_Emergency_Garage_2mm | CalculatedEstimateApparatusBayStorageAndLockersSteel_Emergency_Garage_2mmInternalMassDef
CS Food Preparation - Gas Cooking | 2021_WA_BuildingCode | Commercial Kitchen | Food Preparation - Gas Cooking | Food preparation | 2021 | WA | BuildingCode | 255 | 178 | 102 | CS Food Preparation - Gas Cooking_2021WABuildingCode | CS Food Preparation - Gas Cooking_2021WABuildingCodeScheduleSet | 50 | 20 | 0.21528 | 275 | 80.5979 | 275 | 80.5979 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1 | Food and beverage service_Kitchens (cooking) | ASHRAEHB2025FundCh18tbl4 | Sendentary work_Restaurant | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Kitchens (cooking)ASHRAEHB2025FundCh18tbl4Sendentary work_RestaurantPeopleDef | NECB-B-Occupancy | CS Food Preparation - Gas CookingActivity | 7.5 | 0.0035394 | 0.12 | 0.0006096 | 0.7 | 0.00033036 |  | Washington State Mechanical Code TABLE 403.3.1.1 | Food and beverage service_Kitchens (cooking) |  |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Kitchens (cooking)Vent | 1.3161 | 14.166 | 0.25 | 0.3 | 0.2 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Food Preparation - Gas CookingElectricalEquipDef | NECB-B-Electric-Equipment | 1.09 | 11.7328 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Food preparation | Washington State Energy Code Commercial TABLE C405.4.2Food preparationLightingDef | NECB-B-Lighting | 10.2784 | 35.07 | 377.4935 | 0.1 | 0.2 | 0.7 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | DOEPrototype | COMNET-REV9California Commercial End-Use Survey (CEUS)DOEPrototypeCS Food Preparation - Gas CookingGasEquipDef | RestaurantFastFood FF_GAS_EQUIP_SCH | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Food preparation | PNNL-NECB 2011DOE_PrototypeSpace Function_Food preparationInfil | Always On | Space Function | Food preparation |  | 2.2 |  | Smooth | 0.0023 | 22.8 | 7656 | 515 | 0.9 | 0.7 | 0.7 | Stainless_Commercial_Kitchen_2mm | CalculatedEstimate | GasCookingEquipmentAndStainlessPrep |  | Stainless_Commercial_Kitchen_2mm | CalculatedEstimateGasCookingEquipmentAndStainlessPrepStainless_Commercial_Kitchen_2mmInternalMassDef
CS Guest Room | 2021_WA_BuildingCode | Hotel/Motel | Guest Room | LargeHotel Guest Room | 2021 | WA | BuildingCode | 78 | 167 | 222 | CS Guest Room_2021WABuildingCode | CS Guest Room_2021WABuildingCodeScheduleSet | 100 | 10 | 0.10764 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Hotels,_motels_resorts_dormitories_Bedroom/living room | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels,_motels_resorts_dormitories_Bedroom/living room COMNET-REV9PeopleDef | HotelLarge GuestRoom_Occ_Sch | CS Guest RoomActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Hotels,_motels_resorts_dormitories_Bedroom/living room |  |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels,_motels_resorts_dormitories_Bedroom/living room Vent | 1.5641 | 16.8363 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Guest RoomElectricalEquipDef | HotelLarge GuestRoom_Eqp_Sch_Adva | 0.41 | 4.4132 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Guest room | Washington State Energy Code Commercial TABLE C405.4.2Guest roomLightingDef | HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | [11 empty] | 0.112 |  | 5.2858e-05 | PNNL- | 90.1-2013 | DOE_Prototype | LargeHotel_GuestRoom | PNNL-90.1-2013DOE_PrototypeLargeHotel_GuestRoomInfil | HotelLarge INFIL_QUARTER_ON_SCH | LargeHotel | GuestRoom |  | 1.79 |  | MediumRough | 0.0097 | 3.27 | 1155 | 1293 | 0.9 | 0.7 | 0.65 | Mixed_Hotel_Furniture_10mm | CalculatedEstimate | BedDresserAndCaseGoods |  | Mixed_Hotel_Furniture_10mm | CalculatedEstimateBedDresserAndCaseGoodsMixed_Hotel_Furniture_10mmInternalMassDef
CS Judges Chambers | 2021_WA_BuildingCode | Courthouse | Judges Chambers | Courthouse - chambers | 2021 | WA | BuildingCode | 153 | 153 | 0 | CS Judges Chambers_2021WABuildingCode | CS Judges Chambers_2021WABuildingCodeScheduleSet | 200 | 5 | 0.05382 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Office_Office spaces | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Office_Office spacesCOMNET-REV9PeopleDef | NECB-A-Occupancy | CS Judges ChambersActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Office_Office spaces |  |  | Washington State Mechanical Code TABLE 403.3.1.1Office_Office spacesVent | 1.4928 | 16.0688 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Judges ChambersElectricalEquipDef | NECB-A-Electric-Equipment | 0.74 | 7.9654 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Office - Enclosed <= 250 | Washington State Energy Code Commercial TABLE C405.4.2Office - Enclosed <= 250LightingDef | NECB-A-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Courthouse - chambers | PNNL-NECB 2011DOE_PrototypeSpace Function_Courthouse - chambersInfil | Always On | Space Function | Courthouse - chambers |  | 4.06 |  | MediumRough | 0.0062 | 4.93 | 1520 | 1343 | 0.9 | 0.7 | 0.65 | Wood_Legal_Library_6mm | CalculatedEstimate | LawBookShelvingAndExecutiveFurniture |  | Wood_Legal_Library_6mm | CalculatedEstimateLawBookShelvingAndExecutiveFurnitureWood_Legal_Library_6mmInternalMassDef
CS Laboratory - Classrooms | 2021_WA_BuildingCode | School/University | Laboratory - Classrooms | Lab - classrooms | 2021 | WA | BuildingCode | 224 | 224 | 224 | CS Laboratory - Classrooms _2021WABuildingCode | CS Laboratory - Classrooms _2021WABuildingCodeScheduleSet | 40 | 25 | 0.2691 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Education - Science laboratories | COMNET-REV9 | BA School/University | Washington State Mechanical Code TABLE 403.3.1.1Education - Science laboratoriesCOMNET-REV9BA School/UniversityPeopleDef | NECB-D-Occupancy | CS Laboratory - Classrooms Activity | 10 | 0.0047192 | 0.18 | 0.0009144 | 1 | 0.00047195 |  | Washington State Mechanical Code TABLE 403.3.1.1 | Education - Science laboratories |  |  | Washington State Mechanical Code TABLE 403.3.1.1Education - Science laboratoriesVent | 3.3415 | 35.9683 | 0.2 | 0.5 | 0.1 | COMNET-REV9 |  | Estimate | COMNET-REV9EstimateCS Laboratory - Classrooms ElectricalEquipDef | NECB-D-Electric-Equipment | 1.11 | 11.948 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Laboratory - In or as a classrooms | Washington State Energy Code Commercial TABLE C405.4.2Laboratory - In or as a classroomsLightingDef | NECB-D-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Lab - classrooms | PNNL-NECB 2011DOE_PrototypeSpace Function_Lab - classroomsInfil | Always On | Space Function | Lab - classrooms |  | 3.6 |  | Smooth | 0.0017 | 32.4 | 4900 | 833 | 0.9 | 0.7 | 0.7 | Steel_Lab_Equipment_2mm | CalculatedEstimate | LabBenchesFumeHoodAndStorage |  | Steel_Lab_Equipment_2mm | CalculatedEstimateLabBenchesFumeHoodAndStorageSteel_Lab_Equipment_2mmInternalMassDef
CS Laboratory - Other | 2021_WA_BuildingCode | Laboratory | Laboratory - Other | Lab - research | 2021 | WA | BuildingCode | 224 | 224 | 224 | CS Laboratory - Other_2021WABuildingCode | CS Laboratory - Other_2021WABuildingCodeScheduleSet | 40 | 25 | 0.2691 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Education - Science laboratories | COMNET-REV9 | BA School/University | Washington State Mechanical Code TABLE 403.3.1.1Education - Science laboratoriesCOMNET-REV9BA School/UniversityPeopleDef | NECB-A-Occupancy | CS Laboratory - OtherActivity | 10 | 0.0047192 | 0.18 | 0.0009144 | 1 | 0.00047195 |  | Washington State Mechanical Code TABLE 403.3.1.1 | Education - Science laboratories |  |  | Washington State Mechanical Code TABLE 403.3.1.1Education - Science laboratoriesVent | 3.3415 | 35.9683 | 0.2 | 0.5 | 0.1 | COMNET-REV9 |  | Estimate | COMNET-REV9EstimateCS Laboratory - OtherElectricalEquipDef | NECB-A-Electric-Equipment | 1.33 | 14.3161 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Laboratory - Otherwise | Washington State Energy Code Commercial TABLE C405.4.2Laboratory - OtherwiseLightingDef | NECB-A-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Lab - research | PNNL-NECB 2011DOE_PrototypeSpace Function_Lab - researchInfil | Always On | Space Function | Lab - research |  | 4.53 |  | Smooth | 0.0023 | 34.2 | 6792 | 592 | 0.9 | 0.7 | 0.7 | Steel_Research_Lab_2mm | CalculatedEstimate | ResearchBenchesFumeHoodsAndStorage |  | Steel_Research_Lab_2mm | CalculatedEstimateResearchBenchesFumeHoodsAndStorageSteel_Research_Lab_2mmInternalMassDef
CS Laundry/Washing Area | 2021_WA_BuildingCode | Commercial Laundry | Laundry/Washing Area | SmallHotel Laundry | 2021 | WA | BuildingCode | 120 | 149 | 230 | CS Laundry/Washing Area_2021WABuildingCode | CS Laundry/Washing Area_2021WABuildingCodeScheduleSet | 100 | 10 | 0.10764 | 275 | 80.5979 | 275 | 80.5979 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1 | Dry cleaners, laundries - Commercial laundry | ASHRAEHB2025FundCh18tbl4 | Sendentary work_Restaurant | Washington State Mechanical Code TABLE 403.3.1.1Dry cleaners, laundries - Commercial laundryASHRAEHB2025FundCh18tbl4Sendentary work_RestaurantPeopleDef | HotelSmall LaundryRoom_Occ_Sch | CS Laundry/Washing AreaActivity | 5 | 0.0023596 | 0.12 | 0.0006096 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Dry cleaners, laundries - Commercial laundry |  |  | Washington State Mechanical Code TABLE 403.3.1.1Dry cleaners, laundries - Commercial laundryVent | 0.51912 | 5.5878 | 0.2 | 0.2 | 0.4 | COMNET-REV9 |  | Estimate | COMNET-REV9EstimateCS Laundry/Washing AreaElectricalEquipDef | HotelSmall LaundryRoom_Eqp_Elec_Sch | 0.53 | 5.7049 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Laundry/washing area | Washington State Energy Code Commercial TABLE C405.4.2Laundry/washing areaLightingDef | HotelSmall BLDG_LIGHT_LAUNDRY_SCH | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Hospital - laundry/washing | PNNL-NECB 2011DOE_PrototypeSpace Function_Hospital - laundry/washingInfil | Always On | Space Function | Hospital - laundry/washing |  | 1.92 |  | Smooth | 0.0023 | 27.1 | 6662 | 565 | 0.9 | 0.7 | 0.7 | Steel_Laundry_Equipment_2mm | CalculatedEstimate | CommercialWashersAndDryers |  | Steel_Laundry_Equipment_2mm | CalculatedEstimateCommercialWashersAndDryersSteel_Laundry_Equipment_2mmInternalMassDef
CS Loading Dock - Interior | 2021_WA_BuildingCode | Warehouse | Loading Dock - Interior | Warehouse - med/blk | 2021 | WA | BuildingCode | 153 | 153 | 255 | CS Loading Dock - Interior_2021WABuildingCode | CS Loading Dock - Interior_2021WABuildingCodeScheduleSet | 500 | 2 | 0.021528 | 275 | 80.5979 | 475 | 139.2145 | 219.8124 | 97 | 120 | 0.36667 | Washington State Mechanical Code TABLE 403.3.1.1 | Retail stores, sales floors, and showroom floors - Shipping and receiving | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Shipping and receivingCOMNET-REV9PeopleDef | NECB-A-Occupancy | CS Loading Dock - InteriorActivity | 10 | 0.0047192 | 0.12 | 0.0006096 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Retail stores, sales floors, and showroom floors - Shipping and receiving |  |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Shipping and receivingVent | 0.1 | 1.0764 | 0 | 0.5 | 0 |  |  | DOEPrototype | DOEPrototypeCS Loading Dock - InteriorElectricalEquipDef | NECB-A-Electric-Equipment | 0.88 | 9.4723 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Loading dock, interior | Washington State Energy Code Commercial TABLE C405.4.2Loading dock, interiorLightingDef | NECB-A-Lighting | [11 empty] | 0.2 |  | 9.4389e-05 | Estimate |  |  | Space Function_Warehouse - med/blk | EstimateSpace Function_Warehouse - med/blkInfil | Always On | Space Function | Warehouse - med/blk |  | 1.07 |  | MediumRough | 0.0036 | 75.6 | 6355 | 589 | 0.9 | 0.7 | 0.7 | Steel_Warehouse_Equipment_4mm | CalculatedEstimate | PalletRackingAndDockEquipment |  | Steel_Warehouse_Equipment_4mm | CalculatedEstimatePalletRackingAndDockEquipmentSteel_Warehouse_Equipment_4mmInternalMassDef
CS Lobby - Assisted Living | 2021_WA_BuildingCode | Hotel/Motel | Lobby | Hotel/Motel - lobby | 2021 | WA | BuildingCode | 230 | 157 | 120 | CS Lobby - Assisted Living_2021WABuildingCode | CS Lobby - Assisted Living_2021WABuildingCodeScheduleSet | 33.3333 | 30 | 0.32292 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Hotels, motels, resorts and dormitories - Lobbies/prefunction | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Lobbies/prefunctionCOMNET-REV9PeopleDef | NECB-H-Occupancy | CS Lobby - Assisted LivingActivity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Hotels, motels, resorts and dormitories - Lobbies/prefunction |  |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Lobbies/prefunctionVent | 1.4046 | 15.1196 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Lobby - Assisted LivingElectricalEquipDef | NECB-H-Electric-Equipment | 1.69 | 18.1912 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Lobby - In a facility for the visually impaired (and not used primarily by the staff) | Washington State Energy Code Commercial TABLE C405.4.2Lobby - In a facility for the visually impaired (and not used primarily by the staff)LightingDef | NECB-H-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Hotel/Motel - lobby | PNNL-NECB 2011DOE_PrototypeSpace Function_Hotel/Motel - lobbyInfil | Always On | Space Function | Hotel/Motel - lobby |  | 2.13 |  | MediumRough | 0.0045 | 4.19 | 1362 | 1313 | 0.9 | 0.7 | 0.65 | Wood_Residential_Lobby_5mm | CalculatedEstimate | ResidentialLoungeFurnitureWithPiano |  | Wood_Residential_Lobby_5mm | CalculatedEstimateResidentialLoungeFurnitureWithPianoWood_Residential_Lobby_5mmInternalMassDef
CS Lobby - Elevator | 2021_WA_BuildingCode | Miscellaneous | Lobby - Elevator | Lobby - elevator | 2021 | WA | BuildingCode | 230 | 157 | 120 | CS Lobby - Elevator _2021WABuildingCode | CS Lobby - Elevator _2021WABuildingCodeScheduleSet | [20 empty] | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Corridors serving other than Group R occupancies |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Corridors serving other than Group R occupanciesVent | 0.3 | 3.2292 | 0 | 0.5 | 0 | COMNET-REV9 | BA Warehouse | WholeBuilding | COMNET-REV9BA WarehouseWholeBuildingCS Lobby - Elevator ElectricalEquipDef | NECB-C-Electric-Equipment | 0.65 | 6.9966 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Lobby - For an elevator | Washington State Energy Code Commercial TABLE C405.4.2Lobby - For an elevatorLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Lobby - elevator | PNNL-NECB 2011DOE_PrototypeSpace Function_Lobby - elevatorInfil | Always On | Space Function | Lobby - elevator |  | 0.55 |  | Smooth | 0.0022 | 65.6 | 3739 | 961 | 0.9 | 0.7 | 0.7 | Metal_Elevator_Lobby_2mm | CalculatedEstimate | MinimalBenchAndDirectoryBoard |  | Metal_Elevator_Lobby_2mm | CalculatedEstimateMinimalBenchAndDirectoryBoardMetal_Elevator_Lobby_2mmInternalMassDef
CS Lobby - Hotel | 2021_WA_BuildingCode | Hotel/Motel | Lobby | LargeHotel Lobby | 2021 | WA | BuildingCode | 230 | 157 | 120 | CS Lobby - Hotel_2021WABuildingCode | CS Lobby - Hotel_2021WABuildingCodeScheduleSet | 33.3333 | 30 | 0.32292 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Hotels, motels, resorts and dormitories - Lobbies/prefunction | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Lobbies/prefunctionCOMNET-REV9PeopleDef | HotelLarge BLDG_OCC_SCH | CS Lobby - HotelActivity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Hotels, motels, resorts and dormitories - Lobbies/prefunction |  |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Lobbies/prefunctionVent | 1.5641 | 16.8363 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Lobby - HotelElectricalEquipDef | HotelLarge BLDG_EQUIP_SCH | 0.51 | 5.4896 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Lobby - In a hotel | Washington State Energy Code Commercial TABLE C405.4.2Lobby - In a hotelLightingDef | HotelLarge BLDG_LIGHT_SCH | [11 empty] | 0.112 |  | 5.2858e-05 | PNNL- | NECB 2011 | DOE_Prototype | LargeHotel_Lobby | PNNL-NECB 2011DOE_PrototypeLargeHotel_LobbyInfil | Always On | LargeHotel | Lobby |  | 1.88 |  | MediumRough | 0.0045 | 4.21 | 1601 | 1121 | 0.9 | 0.7 | 0.65 | Mixed_Hotel_Lobby_5mm | CalculatedEstimate | FrontDeskSofasAndAreaRugs |  | Mixed_Hotel_Lobby_5mm | CalculatedEstimateFrontDeskSofasAndAreaRugsMixed_Hotel_Lobby_5mmInternalMassDef
CS Lobby - Motion Picture Theater | 2021_WA_BuildingCode | Theater | Lobby | Lobby - motion picture | 2021 | WA | BuildingCode | 230 | 157 | 120 | CS Lobby - Motion Picture Theater _2021WABuildingCode | CS Lobby - Motion Picture Theater _2021WABuildingCodeScheduleSet | 6.6667 | 150 | 1.6146 | 225 | 65.9437 | 105 | 30.7737 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1 | Theaters - Lobbies | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Theaters - LobbiesCOMNET-REV9PeopleDef | NECB-C-Occupancy | CS Lobby - Motion Picture Theater Activity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Theaters - Lobbies |  |  | Washington State Mechanical Code TABLE 403.3.1.1Theaters - LobbiesVent | 0.74485 | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Lobby - Motion Picture Theater ElectricalEquipDef | NECB-C-Electric-Equipment | 0.23 | 2.4757 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Lobby - In a motion picture theater | Washington State Energy Code Commercial TABLE C405.4.2Lobby - In a motion picture theaterLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Lobby - motion picture | PNNL-NECB 2011DOE_PrototypeSpace Function_Lobby - motion pictureInfil | Always On | Space Function | Lobby - motion picture |  | 1.32 |  | Smooth | 0.0011 | 42.4 | 5971 | 655 | 0.9 | 0.7 | 0.7 | Steel_Theater_Equipment_1mm | CalculatedEstimate | ConcessionStandAndTicketKiosks |  | Steel_Theater_Equipment_1mm | CalculatedEstimateConcessionStandAndTicketKiosksSteel_Theater_Equipment_1mmInternalMassDef
CS Lobby - Performing Arts Theater | 2021_WA_BuildingCode | Theater | Lobby | Lobby - performance arts | 2021 | WA | BuildingCode | 230 | 157 | 120 | CS Lobby - Performing Arts Theater _2021WABuildingCode | CS Lobby - Performing Arts Theater _2021WABuildingCodeScheduleSet | 6.6667 | 150 | 1.6146 | 225 | 65.9437 | 105 | 30.7737 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1 | Theaters - Lobbies | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Theaters - LobbiesCOMNET-REV9PeopleDef | NECB-C-Occupancy | CS Lobby - Performing Arts Theater Activity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Theaters - Lobbies |  |  | Washington State Mechanical Code TABLE 403.3.1.1Theaters - LobbiesVent | 0.74485 | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Lobby - Performing Arts Theater ElectricalEquipDef | NECB-C-Electric-Equipment | 1.25 | 13.455 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Lobby - In a performing arts theater | Washington State Energy Code Commercial TABLE C405.4.2Lobby - In a performing arts theaterLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Lobby - performance arts | PNNL-NECB 2011DOE_PrototypeSpace Function_Lobby - performance artsInfil | Always On | Space Function | Lobby - performance arts |  | 3.01 |  | MediumRough | 0.0043 | 3.32 | 1416 | 1196 | 0.9 | 0.7 | 0.65 | Mixed_Theater_Lobby_4mm | CalculatedEstimate | CarpetedLobbyWithBarAndSeating |  | Mixed_Theater_Lobby_4mm | CalculatedEstimateCarpetedLobbyWithBarAndSeatingMixed_Theater_Lobby_4mmInternalMassDef
CS Lobby - Other | 2021_WA_BuildingCode | Miscellaneous | Lobby | Lobby - other | 2021 | WA | BuildingCode | 230 | 157 | 120 | CS Lobby - Other_2021WABuildingCode | CS Lobby - Other_2021WABuildingCodeScheduleSet | [20 empty] | 1 | 0.00508 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Elevator lobbies in parking garage |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Elevator lobbies in parking garageVent | [10 empty] | 0.84 | 9.0418 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Lobby - Otherwise | Washington State Energy Code Commercial TABLE C405.4.2Lobby - OtherwiseLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Lobby - other | PNNL-NECB 2011DOE_PrototypeSpace Function_Lobby - otherInfil | Always On | Space Function | Lobby - other |  | 0.71 |  | MediumRough | 0.0029 | 24.6 | 1775 | 1112 | 0.9 | 0.7 | 0.7 | Mixed_Commercial_Lobby_3mm | CalculatedEstimate | BasicReceptionAndWaitingArea |  | Mixed_Commercial_Lobby_3mm | CalculatedEstimateBasicReceptionAndWaitingAreaMixed_Commercial_Lobby_3mmInternalMassDef
CS Locker Room | 2021_WA_BuildingCode | Miscellaneous | Locker Room | Locker room | 2021 | WA | BuildingCode | 0 | 153 | 153 | CS Locker Room_2021WABuildingCode | CS Locker Room_2021WABuildingCodeScheduleSet | [22 empty] | 0.25 | 0.00011799 |  | Washington State Mechanical Code TABLE 403.3.1.1 | Education - Locker/dressing rooms |  |  | Washington State Mechanical Code TABLE 403.3.1.1Education - Locker/dressing roomsVent | 0.1 | 1.0764 | 0.2 | 0.5 | 0.1 |  |  | Estimate | EstimateCS Locker RoomElectricalEquipDef | SchoolSecondary BLDG_EQUIP_SCH | 0.52 | 5.5973 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Locker room | Washington State Energy Code Commercial TABLE C405.4.2Locker roomLightingDef | SchoolSecondary BLDG_LIGHT_GYM_SCH | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Locker room | PNNL-NECB 2011DOE_PrototypeSpace Function_Locker roomInfil | Always On | Space Function | Locker room |  | 3.66 |  | Smooth | 0.0011 | 42.3 | 7003 | 567 | 0.9 | 0.7 | 0.7 | Steel_LockerRoom_1mm | CalculatedEstimate | MetalLockersAndBenches |  | Steel_LockerRoom_1mm | CalculatedEstimateMetalLockersAndBenchesSteel_LockerRoom_1mmInternalMassDef
CS Lounge/Break - Healthcare | 2021_WA_BuildingCode | Healthcare | Lounge/Break | Outpatient Lounge | 2021 | WA | BuildingCode | 230 | 157 | 120 | CS Lounge/Break - Healthcare_2021WABuildingCode | CS Lounge/Break - Healthcare_2021WABuildingCodeScheduleSet | 40 | 25 | 0.2691 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Office - Kitchenettes | COMNET-REV9 | BA Healthcare Clinic | Washington State Mechanical Code TABLE 403.3.1.1Office - KitchenettesCOMNET-REV9BA Healthcare ClinicPeopleDef | OutPatientHealthCare BLDG_OCC_SCH | CS Lounge/Break - HealthcareActivity | 5 | 0.0023596 | 0.06 | 0.0003048 | 0.3 | 0.00014158 |  | Washington State Mechanical Code TABLE 403.3.1.1 | Office - Kitchenettes |  |  | Washington State Mechanical Code TABLE 403.3.1.1Office - KitchenettesVent | 1.2488 | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Lounge/Break - HealthcareElectricalEquipDef | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | 0.42 | 4.5209 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Lounge /breakroom - In a health care facility | Washington State Energy Code Commercial TABLE C405.4.2Lounge /breakroom - In a health care facilityLightingDef | OutPatientHealthCare BLDG_LIGHT_SCH | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Outpatient_Lounge | PNNL-90.1-2013DOE_PrototypeOutpatient_LoungeInfil | OutPatientHealthCare INFIL_SCH | Outpatient | Lounge |  | 2.29 |  | MediumRough | 0.0022 | 15.9 | 2558 | 1034 | 0.9 | 0.7 | 0.7 | Mixed_Healthcare_Lounge_2mm | CalculatedEstimate | KitchenetteAndDiningFurniture |  | Mixed_Healthcare_Lounge_2mm | CalculatedEstimateKitchenetteAndDiningFurnitureMixed_Healthcare_Lounge_2mmInternalMassDef
CS Lounge/Break - Other | 2021_WA_BuildingCode | Miscellaneous | Lounge/Break | Office BreakRoom | 2021 | WA | BuildingCode | 230 | 157 | 120 | CS Lounge/Break - Other_2021WABuildingCode | CS Lounge/Break - Other_2021WABuildingCodeScheduleSet | 40 | 25 | 0.2691 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Office - Kitchenettes | COMNET-REV9 | BA Office | Washington State Mechanical Code TABLE 403.3.1.1Office - KitchenettesCOMNET-REV9BA OfficePeopleDef | OfficeMedium BLDG_OCC_SCH | CS Lounge/Break - OtherActivity | 5 | 0.0023596 | 0.06 | 0.0003048 | 0.3 | 0.00014158 |  | Washington State Mechanical Code TABLE 403.3.1.1 | Office - Kitchenettes |  |  | Washington State Mechanical Code TABLE 403.3.1.1Office - KitchenettesVent | 1.6721 | 17.9987 | 0.25 | 0.3 | 0 | COMNET-REV9 | BA Office | WholeBuilding | COMNET-REV9BA OfficeWholeBuildingCS Lounge/Break - OtherElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 0.59 | 6.3508 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Lounge /breakroom - Otherwise | Washington State Energy Code Commercial TABLE C405.4.2Lounge /breakroom - OtherwiseLightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Office_BreakRoom | PNNL-90.1-2013DOE_PrototypeOffice_BreakRoomInfil | OfficeMedium INFIL_SCH_PNNL | Office | BreakRoom |  | 2.83 |  | Smooth | 0.0019 | 23.7 | 4488 | 869 | 0.9 | 0.7 | 0.7 | Steel_Break_Room_2mm | CalculatedEstimate | VendingMachinesAndKitchenette |  | Steel_Break_Room_2mm | CalculatedEstimateVendingMachinesAndKitchenetteSteel_Break_Room_2mmInternalMassDef
CS Office - Enclosed | 2021_WA_BuildingCode | Office | Office - Enclosed | ClosedOffice | 2021 | WA | BuildingCode | 120 | 230 | 199 | CS Office - Enclosed_2021WABuildingCode | CS Office - Enclosed_2021WABuildingCodeScheduleSet | 200 | 5 | 0.05382 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Office - Office spaces | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Office - Office spacesCOMNET-REV9PeopleDef | OfficeMedium BLDG_OCC_SCH | CS Office - EnclosedActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Office - Office spaces |  |  | Washington State Mechanical Code TABLE 403.3.1.1Office - Office spacesVent | 1.6721 | 17.9987 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Office - EnclosedElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 0.74 | 7.9654 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Office - Enclosed <= 250 | Washington State Energy Code Commercial TABLE C405.4.2Office - Enclosed <= 250LightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Office_ClosedOffice | PNNL-90.1-2013DOE_PrototypeOffice_ClosedOfficeInfil | OfficeMedium INFIL_SCH_PNNL | Office | ClosedOffice |  | 2.99 |  | Smooth | 0.0014 | 23.9 | 4513 | 864 | 0.9 | 0.7 | 0.7 | Steel_Office_Furniture_1mm | CalculatedEstimate | DeskFilingCabinetsAndBookshelf |  | Steel_Office_Furniture_1mm | CalculatedEstimateDeskFilingCabinetsAndBookshelfSteel_Office_Furniture_1mmInternalMassDef
CS Office - Open Plan | 2021_WA_BuildingCode | Office | Office - Open Plan | OpenOffice | 2021 | WA | BuildingCode | 120 | 230 | 199 | CS Office - Open Plan_2021WABuildingCode | CS Office - Open Plan_2021WABuildingCodeScheduleSet | 16.6667 | 60 | 0.64583 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019 | Office Buildings - Telephone/data entry | COMNET-REV9 |  | ASHRAE 62.1-2019Office Buildings - Telephone/data entryCOMNET-REV9PeopleDef | OfficeMedium BLDG_OCC_SCH | CS Office - Open PlanActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | ASHRAE 62.1-2019 | Office Buildings - Telephone/data entry |  |  | ASHRAE 62.1-2019Office Buildings - Telephone/data entryVent | 1.6721 | 17.9987 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Office - Open PlanElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 0.61 | 6.566 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Office - Open plan | Washington State Energy Code Commercial TABLE C405.4.2Office - Open planLightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Office_OpenOffice | PNNL-90.1-2013DOE_PrototypeOffice_OpenOfficeInfil | OfficeMedium INFIL_SCH_PNNL | Office | OpenOffice |  | 3.22 |  | MediumRough | 0.0055 | 8.98 | 2130 | 1138 | 0.9 | 0.7 | 0.7 | Particleboard_Office_Panels_5mm | CalculatedEstimate | CubiclePanelsAndWorkstations |  | Particleboard_Office_Panels_5mm | CalculatedEstimateCubiclePanelsAndWorkstationsParticleboard_Office_Panels_5mmInternalMassDef
CS Parking Area - Interior | 2021_WA_BuildingCode | Parking Garage | Parking Area - Interior | Parking garage space | 2021 | WA | BuildingCode | 153 | 0 | 76 | CS Parking Area - Interior_2021WABuildingCode | CS Parking Area - Interior_2021WABuildingCodeScheduleSet | [22 empty] | 0.75 | 0.00035396 |  | Washington State Mechanical Code TABLE 403.3.1.1 | Storage_Repair garages_enclosed parking garage |  |  | Washington State Mechanical Code TABLE 403.3.1.1Storage_Repair garages_enclosed parking garageVent | 0.3 | 3.2292 | 0 | 0.06 | 0.88 |  |  | Medium Estimate: Workplace, 20% of Spaces with Level 2 Charger12%lost to heat | Medium Estimate: Workplace, 20% of Spaces with Level 2 Charger12%lost to heatCS Parking Area - InteriorElectricalEquipDef | NECB-H-Electric-Equipment | 0.15 | 1.6146 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Parking area, interior | Washington State Energy Code Commercial TABLE C405.4.2Parking area, interiorLightingDef | NECB-H-Lighting | [11 empty] | 0.2 |  | 9.4389e-05 | Estimate |  |  | Space Function_Parking garage space | EstimateSpace Function_Parking garage spaceInfil | Always On | Space Function | Parking garage space |  | 2.68 |  | Smooth | 0.006 | 31.1 | 5865 | 669 | 0.9 | 0.7 | 0.65 | Steel_Vehicles_6mm | CalculatedEstimate | ParkedVehiclesAt60PercentOccupancy |  | Steel_Vehicles_6mm | CalculatedEstimateParkedVehiclesAt60PercentOccupancySteel_Vehicles_6mmInternalMassDef
CS Pharmacy Area | 2021_WA_BuildingCode | Healthcare | Pharmacy Area | Hospital - pharmacy | 2021 | WA | BuildingCode | 255 | 0 | 127 | CS Pharmacy Area_2021WABuildingCode | CS Pharmacy Area_2021WABuildingCodeScheduleSet | 100 | 10 | 0.10764 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Workrooms - Pharmacy (prep area) | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Workrooms - Pharmacy (prep area)COMNET-REV9PeopleDef | NECB-C-Occupancy | CS Pharmacy AreaActivity | 5 | 0.0023596 | 0.18 | 0.0009144 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Workrooms - Pharmacy (prep area) |  |  | Washington State Mechanical Code TABLE 403.3.1.1Workrooms - Pharmacy (prep area)Vent | 0.54928 | 5.9124 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Pharmacy AreaElectricalEquipDef | NECB-C-Electric-Equipment | 1.66 | 17.8682 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Pharmacy area | Washington State Energy Code Commercial TABLE C405.4.2Pharmacy areaLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Hospital - pharmacy | PNNL-NECB 2011DOE_PrototypeSpace Function_Hospital - pharmacyInfil | Always On | Space Function | Hospital - pharmacy |  | 4.02 |  | MediumRough | 0.0026 | 14.3 | 3052 | 1139 | 0.9 | 0.7 | 0.7 | Mixed_Pharmacy_3mm | CalculatedEstimate | MedicationShelvingAndStorageCabinets |  | Mixed_Pharmacy_3mm | CalculatedEstimateMedicationShelvingAndStorageCabinetsMixed_Pharmacy_3mmInternalMassDef
CS Restrooms - Assisted Living | 2021_WA_BuildingCode | Assisted Living | Restrooms | Office Restroom | 2021 | WA | BuildingCode | 169 | 169 | 31 | CS Restrooms - Assisted Living_2021WABuildingCode | CS Restrooms - Assisted Living_2021WABuildingCodeScheduleSet | [24 empty] | 7 | Rule of Thumb | Hotels, motels, resorts and dormitories - Bathrooms/toilets - private | Washington State Mechanical Code TABLE 403.3.1.6 - 25/50 per fixture |  | Rule of ThumbHotels, motels, resorts and dormitories - Bathrooms/toilets - privateWashington State Mechanical Code TABLE 403.3.1.6 - 25/50 per fixtureVent | 1.4046 | 15.1196 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Restrooms - Assisted LivingElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 1.26 | 13.5626 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Restroom - In a facility for the visually impaired (and not used primarily by the staff) | Washington State Energy Code Commercial TABLE C405.4.2Restroom - In a facility for the visually impaired (and not used primarily by the staff)LightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Office_Restroom | PNNL-90.1-2013DOE_PrototypeOffice_RestroomInfil | OfficeMedium INFIL_SCH_PNNL | Office | Restroom |  | 3.22 |  | Smooth | 0.0045 | 7.51 | 2167 | 1148 | 0.9 | 0.7 | 0.7 | Phenolic_Restroom_4mm | CalculatedEstimate | ADAFixturesWithGrabBarsAndShower |  | Phenolic_Restroom_4mm | CalculatedEstimateADAFixturesWithGrabBarsAndShowerPhenolic_Restroom_4mmInternalMassDef
CS Restrooms - Other | 2021_WA_BuildingCode | Miscellaneous | Restrooms | PublicRestroom | 2021 | WA | BuildingCode | 169 | 169 | 31 | CS Restrooms - Other_2021WABuildingCode | CS Restrooms - Other_2021WABuildingCodeScheduleSet | [24 empty] | 12 | Rule of Thumb | Public spaces - Toilet rooms - Public | Washington State Mechanical Code TABLE 403.3.1.6 - 50/70 per fixture |  | Rule of ThumbPublic spaces - Toilet rooms - PublicWashington State Mechanical Code TABLE 403.3.1.6 - 50/70 per fixtureVent | 0.3 | 3.2292 | 0 | 0.5 | 0 | COMNET-REV9 | BA Warehouse | WholeBuilding | COMNET-REV9BA WarehouseWholeBuildingCS Restrooms - OtherElectricalEquipDef | HotelSmall Lobby_Eqp_Sch | 0.63 | 6.7813 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Restroom - Otherwise | Washington State Energy Code Commercial TABLE C405.4.2Restroom - OtherwiseLightingDef | HotelSmall BLDG_LIGHT_RESTROOM_SCH | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | SecondarySchool_Restroom | PNNL-90.1-2013DOE_PrototypeSecondarySchool_RestroomInfil | SchoolSecondary INFIL_SCH_PNNL | SecondarySchool | Restroom |  | 2.36 |  | Smooth | 0.0022 | 13.9 | 4190 | 878 | 0.9 | 0.7 | 0.7 | Mixed_Restroom_2mm | CalculatedEstimate | StandardCommercialFixturesAndPartitions |  | Mixed_Restroom_2mm | CalculatedEstimateStandardCommercialFixturesAndPartitionsMixed_Restroom_2mmInternalMassDef
CS Sales Area | 2021_WA_BuildingCode | Retail | Sales Area | Retail - sales | 2021 | WA | BuildingCode | 102 | 255 | 102 | CS Sales Area_2021WABuildingCode | CS Sales Area_2021WABuildingCodeScheduleSet | 66.6667 | 15 | 0.16146 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Retail stores, sales floors, and showroom floors - Sales | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - SalesCOMNET-REV9PeopleDef | NECB-C-Occupancy | CS Sales AreaActivity | 7.5 | 0.0035394 | 0.12 | 0.0006096 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Retail stores, sales floors, and showroom floors - Sales |  |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - SalesVent | 0.54928 | 5.9124 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Sales AreaElectricalEquipDef | NECB-C-Electric-Equipment | 1.05 | 11.3022 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Sales area | Washington State Energy Code Commercial TABLE C405.4.2Sales areaLightingDef | NECB-C-Lighting | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Retail_Point_of_Sale | PNNL-90.1-2013DOE_PrototypeRetail_Point_of_SaleInfil | Always On | Retail | Point_of_Sale |  | 3.54 |  | MediumRough | 0.0032 | 10.6 | 2496 | 1134 | 0.9 | 0.7 | 0.7 | Mixed_Retail_3mm | CalculatedEstimate | DisplayShelvingAndMerchandiseInventory |  | Mixed_Retail_3mm | CalculatedEstimateDisplayShelvingAndMerchandiseInventoryMixed_Retail_3mmInternalMassDef
CS Seating Area General | 2021_WA_BuildingCode | Miscellaneous | Seating Area General | Sales area | 2021 | WA | BuildingCode | 230 | 196 | 120 | CS Seating Area General_2021WABuildingCode | CS Seating Area General_2021WABuildingCodeScheduleSet | 33.3333 | 30 | 0.32292 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Hotels, motels, resorts and dormitories - Lobbies/prefunction | COMNET-REV9 | BA Hotel | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Lobbies/prefunctionCOMNET-REV9BA HotelPeopleDef | NECB-C-Occupancy | CS Seating Area GeneralActivity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Hotels, motels, resorts and dormitories - Lobbies/prefunction |  |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Lobbies/prefunctionVent | 1.5641 | 16.8363 | 0 | 0.5 | 0 | COMNET-REV9 | BA Hotel | WholeBuilding | COMNET-REV9BA HotelWholeBuildingCS Seating Area GeneralElectricalEquipDef | NECB-C-Electric-Equipment | 0.23 | 2.4757 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Seating area, general | Washington State Energy Code Commercial TABLE C405.4.2Seating area, generalLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Transp. seating | PNNL-NECB 2011DOE_PrototypeSpace Function_Transp. seatingInfil | Always On | Space Function | Transp. seating |  | 2.18 |  | MediumRough | 0.0063 | 6.65 | 1015 | 1349 | 0.9 | 0.7 | 0.7 | Mixed_Seating_6mm | CalculatedEstimate | SofasChairsAndAreaRug |  | Mixed_Seating_6mm | CalculatedEstimateSofasChairsAndAreaRugMixed_Seating_6mmInternalMassDef
CS Stairway | 2021_WA_BuildingCode | Miscellaneous | Stairway | Stair | 2021 | WA | BuildingCode | 230 | 157 | 120 | CS Stairway_2021WABuildingCode | CS Stairway_2021WABuildingCodeScheduleSet | [20 empty] | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Corridors serving other than Group R occupancies |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Corridors serving other than Group R occupanciesVent | 0.3 | 3.2292 | 0 | 0.5 | 0 | COMNET-REV9 | BA Warehouse | WholeBuilding | COMNET-REV9BA WarehouseWholeBuildingCS StairwayElectricalEquipDef | HotelSmall AlwaysOff | 0.49 | 5.2744 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Stairwell | Washington State Energy Code Commercial TABLE C405.4.2StairwellLightingDef | HotelSmall BLDG_LIGHT_STAIR_SCH | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Stairway | PNNL-NECB 2011DOE_PrototypeSpace Function_StairwayInfil | Always On | Space Function | Stairway |  | 1.77 |  | MediumRough | 0.0188 | 9.97 | 3219 | 817 | 0.9 | 0.7 | 0.65 | Concrete_Stairway_19mm | CalculatedEstimate | ConcreteStairsWithHandrailsAndGuardrails |  | Concrete_Stairway_19mm | CalculatedEstimateConcreteStairsWithHandrailsAndGuardrailsConcrete_Stairway_19mmInternalMassDef
CS Storage - Hospital | 2021_WA_BuildingCode | Hospital | Storage | Hospital - medical supply | 2021 | WA | BuildingCode | 102 | 0 | 0 | CS Storage - Hospital_2021WABuildingCode | CS Storage - Hospital_2021WABuildingCodeScheduleSet | [20 empty] | 0.12 | 0.0006096 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Retail stores, sales floors, and showroom floors - Storage rooms |  |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Storage roomsVent | 1.2488 | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Storage - HospitalElectricalEquipDef | NECB-H-Electric-Equipment | 0.38 | 4.0903 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Storage room - All other storage | Washington State Energy Code Commercial TABLE C405.4.2Storage room - All other storageLightingDef | NECB-H-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Storage area | PNNL-NECB 2011DOE_PrototypeSpace Function_Storage areaInfil | Always On | Space Function | Storage area |  | 6.89 |  | Smooth | 0.0022 | 9.22 | 4416 | 928 | 0.9 | 0.7 | 0.7 | Steel_Hospital_Storage_2mm | CalculatedEstimate | MedicalShelvingAndSupplyCarts |  | Steel_Hospital_Storage_2mm | CalculatedEstimateMedicalShelvingAndSupplyCartsSteel_Hospital_Storage_2mmInternalMassDef
CS Storage - >= 50 ft2 | 2021_WA_BuildingCode | Miscellaneous | Storage - >= 50 ft2 | Storage area | 2021 | WA | BuildingCode | 102 | 0 | 0 | CS Storage - >= 50 ft2 _2021WABuildingCode | CS Storage - >= 50 ft2 _2021WABuildingCodeScheduleSet | [20 empty] | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Storage - Warehouses |  |  | Washington State Mechanical Code TABLE 403.3.1.1Storage - WarehousesVent | 0.31395 | 3.3793 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Storage - >= 50 ft2 ElectricalEquipDef | NECB-E-Electric-Equipment | 0.38 | 4.0903 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Storage room - >= 50 ft2 | Washington State Energy Code Commercial TABLE C405.4.2Storage room - >= 50 ft2LightingDef | NECB-E-Lighting | [11 empty] | 0.028 |  | 1.3215e-05 | PNNL- | 90.1-2013 | DOE_Prototype | SmallHotel_Storage4Front | PNNL-90.1-2013DOE_PrototypeSmallHotel_Storage4FrontInfil | Always On | SmallHotel | Storage4Front |  | 7.37 |  | MediumRough | 0.004 | 10.9 | 2584 | 1123 | 0.9 | 0.7 | 0.7 | Mixed_Commercial_Storage_4mm | CalculatedEstimate | ShelvingWithFileAndPaperBoxes |  | Mixed_Commercial_Storage_4mm | CalculatedEstimateShelvingWithFileAndPaperBoxesMixed_Commercial_Storage_4mmInternalMassDef
CS Storage - < 50 ft2 | 2021_WA_BuildingCode | Miscellaneous | Storage - < 50 ft2 | Storage area | 2021 | WA | BuildingCode | 102 | 0 | 0 | CS Storage - < 50 ft2 _2021WABuildingCode | CS Storage - < 50 ft2 _2021WABuildingCodeScheduleSet | [20 empty] | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Storage - Warehouses |  |  | Washington State Mechanical Code TABLE 403.3.1.1Storage - WarehousesVent | 0.31395 | 3.3793 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Storage - < 50 ft2 ElectricalEquipDef | NECB-E-Electric-Equipment | 0.51 | 5.4896 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Storage room - < 50 ft2 | Washington State Energy Code Commercial TABLE C405.4.2Storage room - < 50 ft2LightingDef | NECB-E-Lighting | [11 empty] | 0.028 |  | 1.3215e-05 | PNNL- | 90.1-2013 | DOE_Prototype | SmallHotel_Storage4Front | PNNL-90.1-2013DOE_PrototypeSmallHotel_Storage4FrontInfil | Always On | SmallHotel | Storage4Front |  | 4.72 |  | MediumRough | 0.0025 | 14.7 | 2644 | 1128 | 0.9 | 0.7 | 0.7 | Mixed_Small_Storage_2mm | CalculatedEstimate | WallShelvingInJanitorialCloset |  | Mixed_Small_Storage_2mm | CalculatedEstimateWallShelvingInJanitorialClosetMixed_Small_Storage_2mmInternalMassDef
CS Vehicular Maintenance | 2021_WA_BuildingCode | Repair Garage | Vehicular Maintenance | Workshop space | 2021 | WA | BuildingCode | 153 | 0 | 76 | CS Vehicular Maintenance_2021WABuildingCode | CS Vehicular Maintenance_2021WABuildingCodeScheduleSet | [22 empty] | 0.75 | 0.00035396 |  | Washington State Mechanical Code TABLE 403.3.1.1 | Storage_Repair garages_enclosed parking garage |  |  | Washington State Mechanical Code TABLE 403.3.1.1Storage_Repair garages_enclosed parking garageVent | 0.50325 | 5.417 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeCS Vehicular MaintenanceElectricalEquipDef | NECB-A-Electric-Equipment | 0.6 | 6.4584 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Vehicular maintenance | Washington State Energy Code Commercial TABLE C405.4.2Vehicular maintenanceLightingDef | NECB-A-Lighting | [11 empty] | 0.2 |  | 9.4389e-05 | Estimate |  |  | Space Function_Parking garage space | EstimateSpace Function_Parking garage spaceInfil | Always On | Space Function | Parking garage space |  | 1.31 |  | Smooth | 0.0045 | 41.4 | 7054 | 551 | 0.9 | 0.7 | 0.7 | Steel_AutoShop_4mm | CalculatedEstimate | VehicleLiftsAndToolChests |  | Steel_AutoShop_4mm | CalculatedEstimateVehicleLiftsAndToolChestsSteel_AutoShop_4mmInternalMassDef
CS Workshop | 2021_WA_BuildingCode | Workshop | Workshop | Workshop space | 2021 | WA | BuildingCode | 160 | 160 | 160 | CS Workshop_2021WABuildingCode | CS Workshop_2021WABuildingCodeScheduleSet | 50 | 20 | 0.21528 | 635 | 186.1079 | 965 | 282.8253 | 468.9332 | 97 | 120 | 0.39688 | Washington State Mechanical Code TABLE 403.3.1.1 | Education - Wood/metal shops | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Education - Wood/metal shopsCOMNET-REV9PeopleDef | NECB-A-Occupancy | CS WorkshopActivity | 10 | 0.0047192 | 0.18 | 0.0009144 | 0.5 | 0.00023597 |  | Washington State Mechanical Code TABLE 403.3.1.1 | Education - Wood/metal shops |  |  | Washington State Mechanical Code TABLE 403.3.1.1Education - Wood/metal shopsVent | 0.42834 | 4.6106 | 0.1 | 0.5 | 0.1 | COMNET-REV9 |  | Estimate | COMNET-REV9EstimateCS WorkshopElectricalEquipDef | NECB-A-Electric-Equipment | 1.26 | 13.5626 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Workshop | Washington State Energy Code Commercial TABLE C405.4.2WorkshopLightingDef | NECB-A-Lighting | [11 empty] | 0.2 |  | 9.4389e-05 | Estimate |  |  | Space Function_Parking garage space | EstimateSpace Function_Parking garage spaceInfil | Always On | Space Function | Parking garage space |  | 2.27 |  | Smooth | 0.0025 | 40.8 | 6533 | 647 | 0.9 | 0.7 | 0.7 | Steel_Workshop_2mm | CalculatedEstimate | MachineToolsAndWorkbenches |  | Steel_Workshop_2mm | CalculatedEstimateMachineToolsAndWorkbenchesSteel_Workshop_2mmInternalMassDef
SS Assisted Living - Chapel | 2021_WA_BuildingCode | Religious | Chapel | Religious - fellowship hall | 2021 | WA | BuildingCode | 255 | 153 | 255 | SS Assisted Living - Chapel_2021WABuildingCode | SS Assisted Living - Chapel_2021WABuildingCodeScheduleSet | 8.3333 | 120 | 1.2917 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Places of religious worship | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Places of religious worshipCOMNET-REV9PeopleDef | NECB-C-Occupancy | SS Assisted Living - ChapelActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Places of religious worship |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Places of religious worshipVent | 1.4046 | 15.1196 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Assisted Living - ChapelElectricalEquipDef | NECB-C-Electric-Equipment | 0.7 | 7.5348 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Facility for the visually impaired - In a chapel (and not used primarily by the staff) | Washington State Energy Code Commercial TABLE C405.4.2Facility for the visually impaired - In a chapel (and not used primarily by the staff)LightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Religious - fellowship hall | PNNL-NECB 2011DOE_PrototypeSpace Function_Religious - fellowship hallInfil | Always On | Space Function | Religious - fellowship hall |  | 3.06 |  | MediumRough | 0.008 | 3.09 | 855 | 1384 | 0.9 | 0.7 | 0.7 | Mixed_Chapel_8mm | CalculatedEstimate | ChapelSeatingAndAltarFurnishings |  | Mixed_Chapel_8mm | CalculatedEstimateChapelSeatingAndAltarFurnishingsMixed_Chapel_8mmInternalMassDef
SS Assisted Living - Recreation Room | 2021_WA_BuildingCode | Assisted Living | Recreation Room | Hospital - lounge/recreation | 2021 | WA | BuildingCode | 255 | 0 | 0 | SS Assisted Living - Recreation Room_2021WABuildingCode | SS Assisted Living - Recreation Room_2021WABuildingCodeScheduleSet | 25 | 40 | 0.43056 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement - Health club/aerobics room | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Health club/aerobics roomCOMNET-REV9PeopleDef | NECB-B-Occupancy | SS Assisted Living - Recreation RoomActivity | 20 | 0.0094384 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement - Health club/aerobics room |  |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Health club/aerobics roomVent | 1.4046 | 15.1196 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Assisted Living - Recreation RoomElectricalEquipDef | NECB-B-Electric-Equipment | 1.77 | 19.0523 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Facility for the visually impaired - In a recreation room (and not used primarily by the staff) | Washington State Energy Code Commercial TABLE C405.4.2Facility for the visually impaired - In a recreation room (and not used primarily by the staff)LightingDef | NECB-B-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Hospital - lounge/recreation | PNNL-NECB 2011DOE_PrototypeSpace Function_Hospital - lounge/recreationInfil | Always On | Space Function | Hospital - lounge/recreation |  | 3.38 |  | MediumRough | 0.0038 | 6.76 | 1572 | 1213 | 0.9 | 0.7 | 0.7 | Mixed_Recreation_4mm | CalculatedEstimate | RecreationRoomFurnitureAndGameTables |  | Mixed_Recreation_4mm | CalculatedEstimateRecreationRoomFurnitureAndGameTablesMixed_Recreation_4mmInternalMassDef
SS Convention Center - Exhibit Space | 2021_WA_BuildingCode | Convention Center | Exhibit Space | Convention centre - exhibit | 2021 | WA | BuildingCode | 204 | 204 | 0 | SS Convention Center - Exhibit Space _2021WABuildingCode | SS Convention Center - Exhibit Space _2021WABuildingCodeScheduleSet | 25 | 40 | 0.43056 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Museums/galleries | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Museums/galleriesCOMNET-REV9PeopleDef | NECB-C-Occupancy | SS Convention Center - Exhibit Space Activity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Museums/galleries |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Museums/galleriesVent | 0.74761 | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Convention Center - Exhibit Space ElectricalEquipDef | NECB-C-Electric-Equipment | 0.61 | 6.566 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Convention center - Exhibit space | Washington State Energy Code Commercial TABLE C405.4.2Convention center - Exhibit spaceLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Convention centre - exhibit | PNNL-NECB 2011DOE_PrototypeSpace Function_Convention centre - exhibitInfil | Always On | Space Function | Convention centre - exhibit |  | 2 |  | MediumRough | 0.0017 | 7.9 | 1757 | 1092 | 0.9 | 0.7 | 0.7 | Mixed_Exhibit_2mm | CalculatedEstimate | ConventionExhibitBoothsAndDisplays |  | Mixed_Exhibit_2mm | CalculatedEstimateConventionExhibitBoothsAndDisplaysMixed_Exhibit_2mmInternalMassDef
SS Dormitory - Living Quarters | 2021_WA_BuildingCode | Dormitory | Living Quarters | Dormitory - living quarters | 2021 | WA | BuildingCode | 176 | 224 | 230 | SS Dormitory - Living Quarters _2021WABuildingCode | SS Dormitory - Living Quarters _2021WABuildingCodeScheduleSet | 50 | 20 | 0.21528 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Hotels, motels, resorts and dormitories - Dormitory sleeping area | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Dormitory sleeping areaCOMNET-REV9PeopleDef | NECB-G-Occupancy | SS Dormitory - Living Quarters Activity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Hotels, motels, resorts and dormitories - Dormitory sleeping area |  |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Dormitory sleeping areaVent | 1.9561 | 21.0558 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Dormitory - Living Quarters ElectricalEquipDef | NECB-G-Electric-Equipment | 0.5 | 5.382 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Dormitory living quarters | Washington State Energy Code Commercial TABLE C405.4.2Dormitory living quartersLightingDef | NECB-G-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Dormitory - living quarters | PNNL-NECB 2011DOE_PrototypeSpace Function_Dormitory - living quartersInfil | Always On | Space Function | Dormitory - living quarters |  | 4.15 |  | MediumRough | 0.0049 | 6.7 | 1266 | 1256 | 0.9 | 0.7 | 0.7 | Mixed_Dormitory_5mm | CalculatedEstimate | DormitoryBedroomFurniture |  | Mixed_Dormitory_5mm | CalculatedEstimateDormitoryBedroomFurnitureMixed_Dormitory_5mmInternalMassDef
SS Fire Station - Sleeping Quarters | 2021_WA_BuildingCode | Fire Station | Sleeping Quarters | Fire station - quarters | 2021 | WA | BuildingCode | 176 | 224 | 230 | SS Fire Station - Sleeping Quarters _2021WABuildingCode | SS Fire Station - Sleeping Quarters _2021WABuildingCodeScheduleSet | 50 | 20 | 0.21528 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Hotels, motels, resorts and dormitories - Dormitory sleeping area | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Dormitory sleeping areaCOMNET-REV9PeopleDef | NECB-G-Occupancy | SS Fire Station - Sleeping Quarters Activity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Hotels, motels, resorts and dormitories - Dormitory sleeping area |  |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Dormitory sleeping areaVent | 1.5404 | 16.5804 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Fire Station - Sleeping Quarters ElectricalEquipDef | NECB-G-Electric-Equipment | 0.23 | 2.4757 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Fire stations - Sleeping quarters | Washington State Energy Code Commercial TABLE C405.4.2Fire stations - Sleeping quartersLightingDef | NECB-G-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Fire station - quarters | PNNL-NECB 2011DOE_PrototypeSpace Function_Fire station - quartersInfil | Always On | Space Function | Fire station - quarters |  | 2.03 |  | Smooth | 0.0015 | 28.4 | 3803 | 996 | 0.9 | 0.7 | 0.7 | Steel_FireStation_2mm | CalculatedEstimate | FireStationBunkAndLockerFurniture |  | Steel_FireStation_2mm | CalculatedEstimateFireStationBunkAndLockerFurnitureSteel_FireStation_2mmInternalMassDef
SS Gymnasium/Fitness Center - Exercise Area | 2021_WA_BuildingCode | Gymnasium | Exercise Area | Gym - fitness | 2021 | WA | BuildingCode | 255 | 0 | 0 | SS Gymnasium/Fitness Center - Exercise Area _2021WABuildingCode | SS Gymnasium/Fitness Center - Exercise Area _2021WABuildingCodeScheduleSet | 25 | 40 | 0.43056 | 710 | 208.0891 | 1090 | 319.4607 | 527.5498 | 97 | 120 | 0.39444 | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement - Health club/aerobics room | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Health club/aerobics roomCOMNET-REV9PeopleDef | NECB-B-Occupancy | SS Gymnasium/Fitness Center - Exercise Area Activity | 20 | 0.0094384 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement - Health club/aerobics room |  |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Health club/aerobics roomVent | 0.67425 | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Gymnasium/Fitness Center - Exercise Area ElectricalEquipDef | NECB-B-Electric-Equipment | 0.9 | 9.6876 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Gymnasium/fitness center - In an exercise area | Washington State Energy Code Commercial TABLE C405.4.2Gymnasium/fitness center - In an exercise areaLightingDef | NECB-B-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Gym - fitness | PNNL-NECB 2011DOE_PrototypeSpace Function_Gym - fitnessInfil | Always On | Space Function | Gym - fitness |  | 1.79 |  | Smooth | 0.0024 | 50.2 | 6774 | 571 | 0.9 | 0.7 | 0.7 | Steel_Iron_Gym_2mm | CalculatedEstimate | FreeWeightsAndExerciseEquipment |  | Steel_Iron_Gym_2mm | CalculatedEstimateFreeWeightsAndExerciseEquipmentSteel_Iron_Gym_2mmInternalMassDef
SS Gymnasium/Fitness Center - Playing Area | 2021_WA_BuildingCode | Gymnasium | Playing Area | Gym - fitness | 2021 | WA | BuildingCode | 255 | 0 | 0 | SS Gymnasium/Fitness Center - Playing Area _2021WABuildingCode | SS Gymnasium/Fitness Center - Playing Area _2021WABuildingCodeScheduleSet | 142.8571 | 7 | 0.075347 | 710 | 208.0891 | 1090 | 319.4607 | 527.5498 | 97 | 120 | 0.39444 | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement - Gym, stadium, arena (play area) | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Gym, stadium, arena (play area)COMNET-REV9PeopleDef | NECB-B-Occupancy | SS Gymnasium/Fitness Center - Playing Area Activity | 20 | 0.0094384 | 0.18 | 0.0009144 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement - Gym, stadium, arena (play area) |  |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Gym, stadium, arena (play area)Vent | 0.67425 | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Gymnasium/Fitness Center - Playing Area ElectricalEquipDef | NECB-B-Electric-Equipment | 0.85 | 9.1494 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Gymnasium/fitness center - In a playing area | Washington State Energy Code Commercial TABLE C405.4.2Gymnasium/fitness center - In a playing areaLightingDef | NECB-B-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Gym - fitness | PNNL-NECB 2011DOE_PrototypeSpace Function_Gym - fitnessInfil | Always On | Space Function | Gym - fitness |  | 0.5 |  | Smooth | 0.0013 | 45.2 | 6107 | 662 | 0.9 | 0.7 | 0.7 | Steel_Gym_1mm | CalculatedEstimate | GymnasiumPlayingFloorEquipment |  | Steel_Gym_1mm | CalculatedEstimateGymnasiumPlayingFloorEquipmentSteel_Gym_1mmInternalMassDef
SS Healthcare - Emergency Room | 2021_WA_BuildingCode | Hospital | Emergency Room | Hospital - emergency | 2021 | WA | BuildingCode | 255 | 215 | 0 | SS Healthcare - Emergency Room_2021WABuildingCode | SS Healthcare - Emergency Room_2021WABuildingCodeScheduleSet | 50 | 20 | 0.21528 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019 | Outpatient Health Care Facilities - Urgent care triage room | COMNET-REV9 |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care triage roomCOMNET-REV9PeopleDef | NECB-H-Occupancy | SS Healthcare - Emergency RoomActivity | 10 | 0.0047192 | 0.18 | 0.0009144 |  |  |  | ASHRAE 62.1-2019 | Outpatient Health Care Facilities - Urgent care triage room |  |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care triage roomVent | 1.2488 | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Healthcare - Emergency RoomElectricalEquipDef | NECB-H-Electric-Equipment | 1.4 | 15.0696 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Health care facility - In an exam/treatment room | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In an exam/treatment roomLightingDef | NECB-H-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Hospital - emergency | PNNL-NECB 2011DOE_PrototypeSpace Function_Hospital - emergencyInfil | Always On | Space Function | Hospital - emergency |  | 1.89 |  | Smooth | 0.0011 | 24.8 | 4004 | 914 | 0.9 | 0.7 | 0.7 | Steel_Medical_1mm | CalculatedEstimate | EmergencyRoomMedicalEquipment |  | Steel_Medical_1mm | CalculatedEstimateEmergencyRoomMedicalEquipmentSteel_Medical_1mmInternalMassDef
SS Healthcare - Exam/Treatment | 2021_WA_BuildingCode | Healthcare | Exam/Treatment | Outpatient Exam | 2021 | WA | BuildingCode | 136 | 78 | 222 | SS Healthcare - Exam/Treatment _2021WABuildingCode | SS Healthcare - Exam/Treatment _2021WABuildingCodeScheduleSet | 50 | 20 | 0.21528 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019 | Outpatient Health Care Facilities - Urgent care treatment room | COMNET-REV9 |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care treatment roomCOMNET-REV9PeopleDef | OutPatientHealthCare BLDG_OCC_SCH | SS Healthcare - Exam/Treatment Activity | 7.5 | 0.0035394 | 0.18 | 0.0009144 |  |  |  | ASHRAE 62.1-2019 | Outpatient Health Care Facilities - Urgent care treatment room |  |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care treatment roomVent | 1.2488 | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Healthcare - Exam/Treatment ElectricalEquipDef | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | 1.4 | 15.0696 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Health care facility - In an exam/treatment room | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In an exam/treatment roomLightingDef | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Outpatient_Exam | PNNL-90.1-2013DOE_PrototypeOutpatient_ExamInfil | OutPatientHealthCare INFIL_SCH | Outpatient | Exam |  | 2.3 |  | Smooth | 0.00094 | 30.3 | 4812 | 902 | 0.9 | 0.7 | 0.7 | Steel_MedExam_1mm | CalculatedEstimate | ExamTreatmentRoomEquipment |  | Steel_MedExam_1mm | CalculatedEstimateExamTreatmentRoomEquipmentSteel_MedExam_1mmInternalMassDef
SS Healthcare - Supply Room | 2021_WA_BuildingCode | Healthcare | Supply Room | Hospital - medical supply | 2021 | WA | BuildingCode | 0 | 128 | 128 | SS Healthcare - Supply Room_2021WABuildingCode | SS Healthcare - Supply Room_2021WABuildingCodeScheduleSet | [20 empty] | 0.12 | 0.0006096 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Retail stores, sales floors, and showroom floors - Storage rooms |  |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Storage roomsVent | 1.2488 | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Healthcare - Supply RoomElectricalEquipDef | NECB-H-Electric-Equipment | 0.62 | 6.6737 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Health care facility - In a medical supply room | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In a medical supply roomLightingDef | NECB-H-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Hospital_Hospital - medical supply | PNNL-NECB 2011DOE_PrototypeHospital_Hospital - medical supplyInfil | Always On | Hospital | Hospital - medical supply |  | 5.95 |  | Smooth | 0.0017 | 29.9 | 4600 | 860 | 0.9 | 0.7 | 0.7 | Steel_MedSupply_2mm | CalculatedEstimate | MedicalSupplyShelvingAndCarts |  | Steel_MedSupply_2mm | CalculatedEstimateMedicalSupplyShelvingAndCartsSteel_MedSupply_2mmInternalMassDef
SS Healthcare - Nursery | 2021_WA_BuildingCode | Healthcare | Nursery | ICU_Open | 2021 | WA | BuildingCode | 78 | 167 | 222 | SS Healthcare - Nursery _2021WABuildingCode | SS Healthcare - Nursery _2021WABuildingCodeScheduleSet | 50 | 20 | 0.21528 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019 | Outpatient Health Care Facilities - Urgent care observation room | COMNET-REV9 |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care observation roomCOMNET-REV9PeopleDef | Hospital BLDG_OCC_EXTD_SCH | SS Healthcare - Nursery Activity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | ASHRAE 62.1-2019 | Outpatient Health Care Facilities - Urgent care observation room |  |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care observation roomVent | 1.2488 | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Healthcare - Nursery ElectricalEquipDef | Hospital BLDG_EQUIP_EXTD_SCH | 0.92 | 9.9029 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Health care facility - In a nursery | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In a nurseryLightingDef | Hospital BLDG_LIGHT_EXTD_SCH | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Hospital_ICU_Open | PNNL-90.1-2013DOE_PrototypeHospital_ICU_OpenInfil | Hospital INFIL_SCH_PNNL | Hospital | ICU_Open |  | 2.48 |  | Smooth | 0.0012 | 41.5 | 3996 | 921 | 0.9 | 0.7 | 0.7 | Steel_Nursery_1mm | CalculatedEstimate | NurseryBassinetsAndEquipment |  | Steel_Nursery_1mm | CalculatedEstimateNurseryBassinetsAndEquipmentSteel_Nursery_1mmInternalMassDef
SS Healthcare - Nurses’ Station | 2021_WA_BuildingCode | Healthcare | Nurses’ Station | Hospital NurseStn | 2021 | WA | BuildingCode | 31 | 162 | 169 | SS Healthcare - Nurses’ Station _2021WABuildingCode | SS Healthcare - Nurses’ Station _2021WABuildingCodeScheduleSet | 16.6667 | 60 | 0.64583 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019 | Office Buildings - Telephone/data entry | COMNET-REV9 |  | ASHRAE 62.1-2019Office Buildings - Telephone/data entryCOMNET-REV9PeopleDef | Hospital BLDG_OCC_SCH | SS Healthcare - Nurses’ Station Activity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | ASHRAE 62.1-2019 | Office Buildings - Telephone/data entry |  |  | ASHRAE 62.1-2019Office Buildings - Telephone/data entryVent | 1.2488 | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Healthcare - Nurses’ Station ElectricalEquipDef | Hospital BLDG_EQUIP_SCH | 1.17 | 12.5939 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Health care facility - In a nurse's station | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In a nurse's stationLightingDef | Hospital BLDG_LIGHT_NURSEFLR234_SCH | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Hospital_Hospital NurseStn | PNNL-90.1-2013DOE_PrototypeHospital_Hospital NurseStnInfil | Hospital INFIL_SCH_PNNL | Hospital | Hospital NurseStn |  | 3.71 |  | MediumRough | 0.0015 | 20.2 | 3433 | 958 | 0.9 | 0.7 | 0.7 | Mixed_NurseStation_2mm | CalculatedEstimate | NursesStationDeskAndEquipment |  | Mixed_NurseStation_2mm | CalculatedEstimateNursesStationDeskAndEquipmentMixed_NurseStation_2mmInternalMassDef
SS Healthcare - Operating Room | 2021_WA_BuildingCode | Healthcare | Operating Room | Hospital OR | 2021 | WA | BuildingCode | 169 | 31 | 159 | SS Healthcare - Operating Room _2021WABuildingCode | SS Healthcare - Operating Room _2021WABuildingCodeScheduleSet | 50 | 20 | 0.21528 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019 | Outpatient Health Care Facilities - Dental operatory | COMNET-REV9 |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Dental operatoryCOMNET-REV9PeopleDef | Hospital BLDG_OCC_EXTD_SCH | SS Healthcare - Operating Room Activity | 10 | 0.0047192 | 0.18 | 0.0009144 |  |  |  | ASHRAE 62.1-2019 | Outpatient Health Care Facilities - Dental operatory |  |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Dental operatoryVent | 1.2488 | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Healthcare - Operating Room ElectricalEquipDef | Hospital BLDG_EQUIP_EXTD_SCH | 2.26 | 24.3266 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Health care facility - In an operating room | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In an operating roomLightingDef | Hospital BLDG_LIGHT_EXTD_SCH | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Hospital_Hospital OR | PNNL-90.1-2013DOE_PrototypeHospital_Hospital ORInfil | Hospital INFIL_SCH_PNNL | Hospital | Hospital OR |  | 2.81 |  | Smooth | 0.0015 | 62.4 | 6305 | 596 | 0.9 | 0.7 | 0.7 | Steel_Aluminum_OR_2mm | CalculatedEstimate | OperatingRoomStainlessEquipment |  | Steel_Aluminum_OR_2mm | CalculatedEstimateOperatingRoomStainlessEquipmentSteel_Aluminum_OR_2mmInternalMassDef
SS Healthcare - Patient Room | 2021_WA_BuildingCode | Healthcare | Patient Room | Hospital PatRoom | 2021 | WA | BuildingCode | 78 | 167 | 222 | SS Healthcare - Patient Room _2021WABuildingCode | SS Healthcare - Patient Room _2021WABuildingCodeScheduleSet | 50 | 20 | 0.21528 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019 | Outpatient Health Care Facilities - Urgent care observation room | COMNET-REV9 |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care observation roomCOMNET-REV9PeopleDef | Hospital BLDG_OCC_EXTD_SCH | SS Healthcare - Patient Room Activity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | ASHRAE 62.1-2019 | Outpatient Health Care Facilities - Urgent care observation room |  |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care observation roomVent | 1.2488 | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Healthcare - Patient Room ElectricalEquipDef | Hospital BLDG_EQUIP_SCH | 0.68 | 7.3195 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Health care facility - In a patient room | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In a patient roomLightingDef | Hospital BLDG_LIGHT_SCH | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Hospital_Hospital PatRoom | PNNL-90.1-2013DOE_PrototypeHospital_Hospital PatRoomInfil | Hospital INFIL_SCH_PNNL | Hospital | Hospital PatRoom |  | 1.22 |  | MediumRough | 0.0254 | 1.3 | 309 | 718 | 0.9 | 0.7 | 0.7 | Mixed_Healthcare_PatientRoom_25mm | CalculatedEstimate | PatientRoomBedAndFurnishings |  | Mixed_Healthcare_PatientRoom_25mm | CalculatedEstimatePatientRoomBedAndFurnishingsMixed_Healthcare_PatientRoom_25mmInternalMassDef
SS Healthcare - Physical Therapy | 2021_WA_BuildingCode | Healthcare | Physical Therapy | Hospital PhysTherapy | 2021 | WA | BuildingCode | 154 | 230 | 120 | SS Healthcare - Physical Therapy _2021WABuildingCode | SS Healthcare - Physical Therapy _2021WABuildingCodeScheduleSet | 142.8571 | 7 | 0.075347 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019 | Outpatient Health Care Facilities - Physical therapy exercise area | COMNET-REV9 |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Physical therapy exercise areaCOMNET-REV9PeopleDef | Hospital BLDG_OCC_SCH | SS Healthcare - Physical Therapy Activity | 20 | 0.0094384 | 0.18 | 0.0009144 |  |  |  | ASHRAE 62.1-2019 | Outpatient Health Care Facilities - Physical therapy exercise area |  |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Physical therapy exercise areaVent | 1.2488 | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Healthcare - Physical Therapy ElectricalEquipDef | Hospital BLDG_EQUIP_SCH | 0.91 | 9.7952 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Health care facility - In a physical therapy room | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In a physical therapy roomLightingDef | Hospital BLDG_LIGHT_SCH | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Hospital_Hospital PhysTherapy | PNNL-90.1-2013DOE_PrototypeHospital_Hospital PhysTherapyInfil | Hospital INFIL_SCH_PNNL | Hospital | Hospital PhysTherapy |  | 0.89 |  | MediumRough | 0.0166 | 4.21 | 847 | 581 | 0.9 | 0.7 | 0.7 | Mixed_Healthcare_PhysicalTherapy_17mm | CalculatedEstimate | PhysicalTherapyEquipmentAndMats |  | Mixed_Healthcare_PhysicalTherapy_17mm | CalculatedEstimatePhysicalTherapyEquipmentAndMatsMixed_Healthcare_PhysicalTherapy_17mmInternalMassDef
SS Healthcare - Recovery Room | 2021_WA_BuildingCode | Healthcare | Recovery Room | Outpatient PACU | 2021 | WA | BuildingCode | 169 | 31 | 159 | SS Healthcare - Recovery Room_2021WABuildingCode | SS Healthcare - Recovery Room_2021WABuildingCodeScheduleSet | 50 | 20 | 0.21528 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019 | Outpatient Health Care Facilities - Urgent care observation room | COMNET-REV9 |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care observation roomCOMNET-REV9PeopleDef | OutPatientHealthCare BLDG_OCC_SCH | SS Healthcare - Recovery RoomActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | ASHRAE 62.1-2019 | Outpatient Health Care Facilities - Urgent care observation room |  |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care observation roomVent | 1.2488 | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Healthcare - Recovery RoomElectricalEquipDef | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | 1.25 | 13.455 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Health care facility - In a recovery room | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In a recovery roomLightingDef | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | [11 empty] | 0.0446 |  | 2.1049e-05 | PNNL- | 90.1-2013 | DOE_Prototype | Hospital_Outpatient PACU | PNNL-90.1-2013DOE_PrototypeHospital_Outpatient PACUInfil | OutPatientHealthCare INFIL_SCH | Hospital | Outpatient PACU |  | 1.09 |  | MediumRough | 0.0109 | 4.21 | 957 | 661 | 0.9 | 0.7 | 0.7 | Mixed_Healthcare_RecoveryRoom_11mm | CalculatedEstimate | RecoveryRoomBedAndMonitoringEquipment |  | Mixed_Healthcare_RecoveryRoom_11mm | CalculatedEstimateRecoveryRoomBedAndMonitoringEquipmentMixed_Healthcare_RecoveryRoom_11mmInternalMassDef
SS Library - Reading Area | 2021_WA_BuildingCode | Library | Reading Area | Library - reading | 2021 | WA | BuildingCode | 240 | 230 | 140 | SS Library - Reading Area _2021WABuildingCode | SS Library - Reading Area _2021WABuildingCodeScheduleSet | 100 | 10 | 0.10764 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Libraries | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - LibrariesCOMNET-REV9PeopleDef | NECB-C-Occupancy | SS Library - Reading Area Activity | 5 | 0.0023596 | 0.12 | 0.0006096 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Libraries |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - LibrariesVent | 0.93723 | 10.0883 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Library - Reading Area ElectricalEquipDef | NECB-C-Electric-Equipment | 0.96 | 10.3334 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Library - In a reading area | Washington State Energy Code Commercial TABLE C405.4.2Library - In a reading areaLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Library - reading | PNNL-NECB 2011DOE_PrototypeSpace Function_Library - readingInfil | Always On | Space Function | Library - reading |  | 1.54 |  | MediumRough | 0.0221 | 0.18 | 344 | 1399 | 0.9 | 0.7 | 0.7 | Mixed_Library_ReadingArea_22mm | CalculatedEstimate | WoodTablesCarrelsAndSeating |  | Mixed_Library_ReadingArea_22mm | CalculatedEstimateWoodTablesCarrelsAndSeatingMixed_Library_ReadingArea_22mmInternalMassDef
SS Library - Stacks | 2021_WA_BuildingCode | Library | Stacks | Library - stacks | 2021 | WA | BuildingCode | 218 | 165 | 32 | SS Library - Stacks _2021WABuildingCode | SS Library - Stacks _2021WABuildingCodeScheduleSet | 100 | 10 | 0.10764 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Libraries | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - LibrariesCOMNET-REV9PeopleDef | NECB-C-Occupancy | SS Library - Stacks Activity | 5 | 0.0023596 | 0.12 | 0.0006096 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Libraries |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - LibrariesVent | 0.93723 | 10.0883 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Library - Stacks ElectricalEquipDef | NECB-C-Electric-Equipment | 1.1 | 11.8404 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Library - In the stacks | Washington State Energy Code Commercial TABLE C405.4.2Library - In the stacksLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Library - stacks | PNNL-NECB 2011DOE_PrototypeSpace Function_Library - stacksInfil | Always On | Space Function | Library - stacks |  | 8.85 |  | MediumRough | 0.0122 | 1.707 | 1346 | 1140 | 0.9 | 0.7 | 0.7 | Mixed_Library_Stacks_12mm | CalculatedEstimate | SteelShelvingWithBooks |  | Mixed_Library_Stacks_12mm | CalculatedEstimateSteelShelvingWithBooksMixed_Library_Stacks_12mmInternalMassDef
SS Manufacturing Facility - Detailed Manufacturing | 2021_WA_BuildingCode | Manufacturing Facility | Detailed Manufacturing | Mfg - detailed | 2021 | WA | BuildingCode | 127 | 0 | 255 | SS Manufacturing Facility - Detailed Manufacturing _2021WABuildingCode | SS Manufacturing Facility - Detailed Manufacturing _2021WABuildingCodeScheduleSet | 142.8571 | 7 | 0.075347 | 580 | 169.9883 | 870 | 254.9824 | 424.9707 | 97 | 120 | 0.4 | ASHRAE 62.1-2019 | Miscellaneous Spaces - Manufacturing where hazardous materials are not used | COMNET-REV9 |  | ASHRAE 62.1-2019Miscellaneous Spaces - Manufacturing where hazardous materials are not usedCOMNET-REV9PeopleDef | NECB-A-Occupancy | SS Manufacturing Facility - Detailed Manufacturing Activity | 10 | 0.0047192 | 0.18 | 0.0009144 |  |  |  | ASHRAE 62.1-2019 | Miscellaneous Spaces - Manufacturing where hazardous materials are not used |  |  | ASHRAE 62.1-2019Miscellaneous Spaces - Manufacturing where hazardous materials are not usedVent | 0.34481 | 3.7116 | 0.1 | 0.5 | 0.1 | COMNET-REV9 |  | Estimate | COMNET-REV9EstimateSS Manufacturing Facility - Detailed Manufacturing ElectricalEquipDef | NECB-A-Electric-Equipment | 0.8 | 8.6112 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Manufacturing facility - In a detailed manufacturing area | Washington State Energy Code Commercial TABLE C405.4.2Manufacturing facility - In a detailed manufacturing areaLightingDef | NECB-A-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Mfg - detailed | PNNL-NECB 2011DOE_PrototypeSpace Function_Mfg - detailedInfil | Always On | Space Function | Mfg - detailed |  | 1.04 |  | MediumRough | 0.0116 | 40.35 | 6074 | 483 | 0.9 | 0.7 | 0.7 | Mixed_Manufacturing_Detailed_12mm | CalculatedEstimate | CNCMachineToolsAndWorkbenches |  | Mixed_Manufacturing_Detailed_12mm | CalculatedEstimateCNCMachineToolsAndWorkbenchesMixed_Manufacturing_Detailed_12mmInternalMassDef
SS Manufacturing Facility - Equipment Room | 2021_WA_BuildingCode | Manufacturing Facility | Equipment Room | Mfg - equipment | 2021 | WA | BuildingCode | 41 | 31 | 175 | SS Manufacturing Facility - Equipment Room _2021WABuildingCode | SS Manufacturing Facility - Equipment Room _2021WABuildingCodeScheduleSet | 142.8571 | 7 | 0.075347 | 580 | 169.9883 | 870 | 254.9824 | 424.9707 | 97 | 120 | 0.4 | Rule of Thumb | Requires engineering analysis per Section 403.3.1.1 | COMNET-REV9 |  | Rule of ThumbRequires engineering analysis per Section 403.3.1.1COMNET-REV9PeopleDef | NECB-A-Occupancy | SS Manufacturing Facility - Equipment Room Activity | [6 empty] | 6 | Rule of Thumb | Requires engineering analysis per Section 403.3.1.1 |  |  | Rule of ThumbRequires engineering analysis per Section 403.3.1.1Vent | 0.34481 | 3.7116 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Manufacturing Facility - Equipment Room ElectricalEquipDef | NECB-A-Electric-Equipment | 0.76 | 8.1806 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Manufacturing facility - In an equipment room | Washington State Energy Code Commercial TABLE C405.4.2Manufacturing facility - In an equipment roomLightingDef | NECB-A-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Mfg - equipment | PNNL-NECB 2011DOE_PrototypeSpace Function_Mfg - equipmentInfil | Always On | Space Function | Mfg - equipment |  | 0.76 |  | MediumRough | 0.0069 | 40.55 | 4978 | 548 | 0.9 | 0.7 | 0.7 | Mixed_Manufacturing_EquipRoom_7mm | CalculatedEstimate | CompressorsHPUsAndElectricalPanels |  | Mixed_Manufacturing_EquipRoom_7mm | CalculatedEstimateCompressorsHPUsAndElectricalPanelsMixed_Manufacturing_EquipRoom_7mmInternalMassDef
SS Manufacturing Facility - Extra High Bay (>50 ft Floor to Ceiling Height) | 2021_WA_BuildingCode | Manufacturing Facility | Extra High Bay (>50 ft Floor to Ceiling Height) | Mfg - bay H > 15m | 2021 | WA | BuildingCode | 102 | 0 | 204 | SS Manufacturing Facility - Extra High Bay (>50 ft Floor to Ceiling Height) _2021WABuildingCode | SS Manufacturing Facility - Extra High Bay (>50 ft Floor to Ceiling Height) _2021WABuildingCodeScheduleSet | 142.8571 | 7 | 0.075347 | 580 | 169.9883 | 870 | 254.9824 | 424.9707 | 97 | 120 | 0.4 | ASHRAE 62.1-2019 | Miscellaneous Spaces - Manufacturing where hazardous materials are not used - ACH | COMNET-REV9 |  | ASHRAE 62.1-2019Miscellaneous Spaces - Manufacturing where hazardous materials are not used - ACHCOMNET-REV9PeopleDef | NECB-A-Occupancy | SS Manufacturing Facility - Extra High Bay (>50 ft Floor to Ceiling Height) Activity | [6 empty] | 0.09 | ASHRAE 62.1-2019 | Miscellaneous Spaces - Manufacturing where hazardous materials are not used | ACH |  | ASHRAE 62.1-2019Miscellaneous Spaces - Manufacturing where hazardous materials are not usedACHVent | 0.34481 | 3.7116 | 0.1 | 0.5 | 0.1 | COMNET-REV9 |  | Estimate | COMNET-REV9EstimateSS Manufacturing Facility - Extra High Bay (>50 ft Floor to Ceiling Height) ElectricalEquipDef | NECB-A-Electric-Equipment | 1.42 | 15.2849 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Manufacturing facility - In an extra high bay area (> 50-foot floor-ceiling height) | Washington State Energy Code Commercial TABLE C405.4.2Manufacturing facility - In an extra high bay area (> 50-foot floor-ceiling height)LightingDef | NECB-A-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Mfg - bay H > 15m | PNNL-NECB 2011DOE_PrototypeSpace Function_Mfg - bay H > 15mInfil | Always On | Space Function | Mfg - bay H > 15m |  | 0.67 |  | MediumRough | 0.029 | 48.41 | 7474 | 463 | 0.9 | 0.7 | 0.7 | Mixed_Manufacturing_ExtraHighBay_29mm | CalculatedEstimate | OverheadCranesAndHeavyPresses |  | Mixed_Manufacturing_ExtraHighBay_29mm | CalculatedEstimateOverheadCranesAndHeavyPressesMixed_Manufacturing_ExtraHighBay_29mmInternalMassDef
SS Manufacturing Facility - High Bay (25–50 ft Floor to Ceiling Height) | 2021_WA_BuildingCode | Manufacturing Facility | High Bay (25–50 ft Floor to Ceiling Height) | Mfg - 7.5 <= bay H <= 15m | 2021 | WA | BuildingCode | 216 | 191 | 216 | SS Manufacturing Facility - High Bay (25–50 ft Floor to Ceiling Height) _2021WABuildingCode | SS Manufacturing Facility - High Bay (25–50 ft Floor to Ceiling Height) _2021WABuildingCodeScheduleSet | 142.8571 | 7 | 0.075347 | 580 | 169.9883 | 870 | 254.9824 | 424.9707 | 97 | 120 | 0.4 | ASHRAE 62.1-2019 | Miscellaneous Spaces - Manufacturing where hazardous materials are not used - ACH | COMNET-REV9 |  | ASHRAE 62.1-2019Miscellaneous Spaces - Manufacturing where hazardous materials are not used - ACHCOMNET-REV9PeopleDef | NECB-A-Occupancy | SS Manufacturing Facility - High Bay (25–50 ft Floor to Ceiling Height) Activity | [6 empty] | 0.09 | ASHRAE 62.1-2019 | Miscellaneous Spaces - Manufacturing where hazardous materials are not used | ACH |  | ASHRAE 62.1-2019Miscellaneous Spaces - Manufacturing where hazardous materials are not usedACHVent | 0.34481 | 3.7116 | 0.1 | 0.5 | 0.1 | COMNET-REV9 |  | Estimate | COMNET-REV9EstimateSS Manufacturing Facility - High Bay (25–50 ft Floor to Ceiling Height) ElectricalEquipDef | NECB-A-Electric-Equipment | 1.24 | 13.3474 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Manufacturing facility - In a high bay area (25 - 50-foot floor-ceiling height) | Washington State Energy Code Commercial TABLE C405.4.2Manufacturing facility - In a high bay area (25 - 50-foot floor-ceiling height)LightingDef | NECB-A-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Mfg - 7.5 <= bay H <= 15m | PNNL-NECB 2011DOE_PrototypeSpace Function_Mfg - 7.5 <= bay H <= 15mInfil | Always On | Space Function | Mfg - 7.5 <= bay H <= 15m |  | 0.93 |  | MediumRough | 0.0158 | 35.21 | 6079 | 611 | 0.9 | 0.7 | 0.7 | Mixed_Manufacturing_HighBay_16mm | CalculatedEstimate | CranesCuttingTablesAndStorageRacks |  | Mixed_Manufacturing_HighBay_16mm | CalculatedEstimateCranesCuttingTablesAndStorageRacksMixed_Manufacturing_HighBay_16mmInternalMassDef
SS Manufacturing Facility - Low Bay (<25 ft Floor to Ceiling Height) | 2021_WA_BuildingCode | Manufacturing Facility | Low Bay (<25 ft Floor to Ceiling Height) | Mfg - bay H < 7.5m | 2021 | WA | BuildingCode | 221 | 160 | 221 | SS Manufacturing Facility - Low Bay (<25 ft Floor to Ceiling Height) _2021WABuildingCode | SS Manufacturing Facility - Low Bay (<25 ft Floor to Ceiling Height) _2021WABuildingCodeScheduleSet | 142.8571 | 7 | 0.075347 | 580 | 169.9883 | 870 | 254.9824 | 424.9707 | 97 | 120 | 0.4 | ASHRAE 62.1-2019 | Miscellaneous Spaces - Manufacturing where hazardous materials are not used - ACH | COMNET-REV9 |  | ASHRAE 62.1-2019Miscellaneous Spaces - Manufacturing where hazardous materials are not used - ACHCOMNET-REV9PeopleDef | NECB-A-Occupancy | SS Manufacturing Facility - Low Bay (<25 ft Floor to Ceiling Height) Activity | [6 empty] | 0.09 | ASHRAE 62.1-2019 | Miscellaneous Spaces - Manufacturing where hazardous materials are not used | ACH |  | ASHRAE 62.1-2019Miscellaneous Spaces - Manufacturing where hazardous materials are not usedACHVent | 0.34481 | 3.7116 | 0.1 | 0.5 | 0.1 | COMNET-REV9 |  | Estimate | COMNET-REV9EstimateSS Manufacturing Facility - Low Bay (<25 ft Floor to Ceiling Height) ElectricalEquipDef | NECB-A-Electric-Equipment | 0.86 | 9.257 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Manufacturing facility - In a low bay area (< 25-foot floor-ceiling height) | Washington State Energy Code Commercial TABLE C405.4.2Manufacturing facility - In a low bay area (< 25-foot floor-ceiling height)LightingDef | NECB-A-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Mfg - bay H < 7.5m | PNNL-NECB 2011DOE_PrototypeSpace Function_Mfg - bay H < 7.5mInfil | Always On | Space Function | Mfg - bay H < 7.5m |  | 1.21 |  | MediumRough | 0.0121 | 41.22 | 5929 | 485 | 0.9 | 0.7 | 0.7 | Mixed_Manufacturing_LowBay_12mm | CalculatedEstimate | StampingPressesAndInjectionMolders |  | Mixed_Manufacturing_LowBay_12mm | CalculatedEstimateStampingPressesAndInjectionMoldersMixed_Manufacturing_LowBay_12mmInternalMassDef
SS Museum - General Exhibition | 2021_WA_BuildingCode | Museum | General Exhibition | Museum - exhibition | 2021 | WA | BuildingCode | 204 | 204 | 0 | SS Museum - General Exhibition _2021WABuildingCode | SS Museum - General Exhibition _2021WABuildingCodeScheduleSet | 25 | 40 | 0.43056 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Museums/galleries | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Museums/galleriesCOMNET-REV9PeopleDef | NECB-C-Occupancy | SS Museum - General Exhibition Activity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Museums/galleries |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Museums/galleriesVent | 0.74485 | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Museum - General Exhibition ElectricalEquipDef | NECB-C-Electric-Equipment | 0.31 | 3.3368 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Museum - In a general exhibition area | Washington State Energy Code Commercial TABLE C405.4.2Museum - In a general exhibition areaLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Museum - exhibition | PNNL-NECB 2011DOE_PrototypeSpace Function_Museum - exhibitionInfil | Always On | Space Function | Museum - exhibition |  | 1.18 |  | MediumRough | 0.0133 | 5.26 | 846 | 1136 | 0.9 | 0.7 | 0.7 | Mixed_Museum_Exhibition_13mm | CalculatedEstimate | DisplayCasesAndPedestals |  | Mixed_Museum_Exhibition_13mm | CalculatedEstimateDisplayCasesAndPedestalsMixed_Museum_Exhibition_13mmInternalMassDef
SS Museum - Restoration | 2021_WA_BuildingCode | Museum | Restoration | Museum - restoration | 2021 | WA | BuildingCode | 160 | 160 | 160 | SS Museum - Restoration _2021WABuildingCode | SS Museum - Restoration _2021WABuildingCodeScheduleSet | 25 | 40 | 0.43056 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019 | Public Assembly Spaces - Museums (children’s) | COMNET-REV9 |  | ASHRAE 62.1-2019Public Assembly Spaces - Museums (children’s)COMNET-REV9PeopleDef | NECB-A-Occupancy | SS Museum - Restoration Activity | 7.5 | 0.0035394 | 0.12 | 0.0006096 |  |  |  | ASHRAE 62.1-2019 | Public Assembly Spaces - Museums (children’s) |  |  | ASHRAE 62.1-2019Public Assembly Spaces - Museums (children’s)Vent | 0.42834 | 4.6106 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Museum - Restoration ElectricalEquipDef | NECB-A-Electric-Equipment | 1.1 | 11.8404 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Museum - In a restoration room | Washington State Energy Code Commercial TABLE C405.4.2Museum - In a restoration roomLightingDef | NECB-A-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Museum - restoration | PNNL-NECB 2011DOE_PrototypeSpace Function_Museum - restorationInfil | Always On | Space Function | Museum - restoration |  | 1.65 |  | MediumRough | 0.0058 | 12.26 | 2395 | 642 | 0.9 | 0.6 | 0.6 | Mixed_Museum_Restoration_6mm | CalculatedEstimate | SteelCaseworkHoodsAndHardwoodBenches |  | Mixed_Museum_Restoration_6mm | CalculatedEstimateSteelCaseworkHoodsAndHardwoodBenchesMixed_Museum_Restoration_6mmInternalMassDef
SS Post Office - Sorting Area | 2021_WA_BuildingCode | Post Office | Sorting Area | Post office sorting | 2021 | WA | BuildingCode | 245 | 245 | 220 | SS Post Office - Sorting Area _2021WABuildingCode | SS Post Office - Sorting Area _2021WABuildingCodeScheduleSet | 142.8571 | 7 | 0.075347 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019 | Miscellaneous Spaces - Sorting, packing, light assembly | COMNET-REV9 |  | ASHRAE 62.1-2019Miscellaneous Spaces - Sorting, packing, light assemblyCOMNET-REV9PeopleDef | NECB-A-Occupancy | SS Post Office - Sorting Area Activity | 7.5 | 0.0035394 | 0.12 | 0.0006096 |  |  |  | ASHRAE 62.1-2019 | Miscellaneous Spaces - Sorting, packing, light assembly |  |  | ASHRAE 62.1-2019Miscellaneous Spaces - Sorting, packing, light assemblyVent | 1.669 | 17.9649 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Post Office - Sorting Area ElectricalEquipDef | NECB-A-Electric-Equipment | 0.76 | 8.1806 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Post office - Sorting area | Washington State Energy Code Commercial TABLE C405.4.2Post office - Sorting areaLightingDef | NECB-A-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Post office sorting | PNNL-NECB 2011DOE_PrototypeSpace Function_Post office sortingInfil | Always On | Space Function | Post office sorting |  | 3.09 |  | MediumRough | 0.0016 | 42.18 | 6314 | 491 | 0.9 | 0.7 | 0.7 | Mixed_PostOffice_SortingArea_2mm | CalculatedEstimate | FlatSortCasesAndMailHampers |  | Mixed_PostOffice_SortingArea_2mm | CalculatedEstimateFlatSortCasesAndMailHampersMixed_PostOffice_SortingArea_2mmInternalMassDef
SS Religious Building - Fellowship Hall | 2021_WA_BuildingCode | Religious | Fellowship Hall | Religious - fellowship hall | 2021 | WA | BuildingCode | 255 | 153 | 255 | SS Religious Building - Fellowship Hall_2021WABuildingCode | SS Religious Building - Fellowship Hall_2021WABuildingCodeScheduleSet | 8.3333 | 120 | 1.2917 | 245 | 71.8054 | 155 | 45.4279 | 117.2333 | 97 | 120 | 0.6125 | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Places of religious worship | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Places of religious worshipCOMNET-REV9PeopleDef | NECB-C-Occupancy | SS Religious Building - Fellowship HallActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Places of religious worship |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Places of religious worshipVent | 0.29845 | 3.2125 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Religious Building - Fellowship HallElectricalEquipDef | NECB-C-Electric-Equipment | 0.54 | 5.8126 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Religious building - In a fellowship hall | Washington State Energy Code Commercial TABLE C405.4.2Religious building - In a fellowship hallLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Religious - fellowship hall | PNNL-NECB 2011DOE_PrototypeSpace Function_Religious - fellowship hallInfil | Always On | Space Function | Religious - fellowship hall |  | 1.15 |  | MediumRough | 0.0073 | 2.614 | 902 | 1157 | 0.9 | 0.7 | 0.7 | Mixed_ReligiousBuilding_FellowshipHall_7mm | CalculatedEstimate | FoldingTablesAndStackableChairs |  | Mixed_ReligiousBuilding_FellowshipHall_7mm | CalculatedEstimateFoldingTablesAndStackableChairsMixed_ReligiousBuilding_FellowshipHall_7mmInternalMassDef
SS Religious Building - Worship/Pulpit/Choir | 2021_WA_BuildingCode | Religious | Worship/Pulpit/Choir | Religious - pulpit/choir | 2021 | WA | BuildingCode | 255 | 153 | 255 | SS Religious Building - Worship/Pulpit/Choir_2021WABuildingCode | SS Religious Building - Worship/Pulpit/Choir_2021WABuildingCodeScheduleSet | 8.3333 | 120 | 1.2917 | 245 | 71.8054 | 155 | 45.4279 | 117.2333 | 97 | 120 | 0.6125 | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Places of religious worship | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Places of religious worshipCOMNET-REV9PeopleDef | NECB-I-Occupancy | SS Religious Building - Worship/Pulpit/ChoirActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Public spaces - Places of religious worship |  |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Places of religious worshipVent | 0.29845 | 3.2125 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Religious Building - Worship/Pulpit/ChoirElectricalEquipDef | NECB-I-Electric-Equipment | 0.85 | 9.1494 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Religious building - In a worship pulpit/choir area | Washington State Energy Code Commercial TABLE C405.4.2Religious building - In a worship pulpit/choir areaLightingDef | NECB-I-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Religious - pulpit/choir | PNNL-NECB 2011DOE_PrototypeSpace Function_Religious - pulpit/choirInfil | Always On | Space Function | Religious - pulpit/choir |  | 0.88 |  | MediumRough | 0.0208 | 0.251 | 721 | 1568 | 0.9 | 0.7 | 0.7 | Mixed_ReligiousBuilding_WorshipChoir_21mm | CalculatedEstimate | SolidHardwoodPewsAndPulpit |  | Mixed_ReligiousBuilding_WorshipChoir_21mm | CalculatedEstimateSolidHardwoodPewsAndPulpitMixed_ReligiousBuilding_WorshipChoir_21mmInternalMassDef
SS Retail - Dressing/Fitting Room | 2021_WA_BuildingCode | Retail | Dressing/Fitting Room | Retail - dressing/fitting | 2021 | WA | BuildingCode | 230 | 230 | 250 | SS Retail - Dressing/Fitting Room _2021WABuildingCode | SS Retail - Dressing/Fitting Room _2021WABuildingCodeScheduleSet | [22 empty] | 0.25 | 0.00011799 |  | Washington State Mechanical Code TABLE 403.3.1.1 | Retail stores, sales floors, and showroom floors - Dressing rooms |  |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Dressing roomsVent | 0.82157 | 8.8434 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Retail - Dressing/Fitting Room ElectricalEquipDef | NECB-C-Electric-Equipment | 0.51 | 5.4896 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Retail - In a dressing/fitting room | Washington State Energy Code Commercial TABLE C405.4.2Retail - In a dressing/fitting roomLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Retail - dressing/fitting | PNNL-NECB 2011DOE_PrototypeSpace Function_Retail - dressing/fittingInfil | Always On | Space Function | Retail - dressing/fitting |  | 3.91 |  | MediumRough | 0.0092 | 0.668 | 773 | 1222 | 0.9 | 0.7 | 0.7 | Mixed_Retail_DressingRoom_9mm | CalculatedEstimate | MDFStallPartitionsAndMirrors |  | Mixed_Retail_DressingRoom_9mm | CalculatedEstimateMDFStallPartitionsAndMirrorsMixed_Retail_DressingRoom_9mmInternalMassDef
SS Retail - Mall Concourse | 2021_WA_BuildingCode | Retail | Mall Concourse | Retail - mall concourse | 2021 | WA | BuildingCode | 176 | 196 | 222 | SS Retail - Mall Concourse _2021WABuildingCode | SS Retail - Mall Concourse _2021WABuildingCodeScheduleSet | 25 | 40 | 0.43056 | 250 | 73.2708 | 200 | 58.6166 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1 | Retail stores, sales floors, and showroom floors - Mall common areas | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Mall common areasCOMNET-REV9PeopleDef | NECB-C-Occupancy | SS Retail - Mall Concourse Activity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Retail stores, sales floors, and showroom floors - Mall common areas |  |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Mall common areasVent | 0 | 0 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Retail - Mall Concourse ElectricalEquipDef | NECB-C-Electric-Equipment | 0.82 | 8.8265 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Retail - In a mall concourse | Washington State Energy Code Commercial TABLE C405.4.2Retail - In a mall concourseLightingDef | NECB-C-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Retail - mall concourse | PNNL-NECB 2011DOE_PrototypeSpace Function_Retail - mall concourseInfil | Always On | Space Function | Retail - mall concourse |  | 0.4 |  | MediumRough | 0.0192 | 5.444 | 1338 | 1154 | 0.9 | 0.7 | 0.7 | Mixed_Retail_MallConcourse_19mm | CalculatedEstimate | KiosksBenchesAndConcretePlanters |  | Mixed_Retail_MallConcourse_19mm | CalculatedEstimateKiosksBenchesAndConcretePlantersMixed_Retail_MallConcourse_19mmInternalMassDef
SS Sports Arena Playing Area - Class I | 2021_WA_BuildingCode | Sports Arena | Playing Area - Class I | Sports arena - court c1 | 2021 | WA | BuildingCode | 127 | 255 | 212 | SS Sports Arena Playing Area - Class I _2021WABuildingCode | SS Sports Arena Playing Area - Class I _2021WABuildingCodeScheduleSet | 6.6667 | 150 | 1.6146 | 245 | 71.8054 | 105 | 30.7737 | 102.5791 | 97 | 120 | 0.7 | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement - Spectator areas | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Spectator areasCOMNET-REV9PeopleDef | NECB-B-Occupancy | SS Sports Arena Playing Area - Class I Activity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement - Spectator areas |  |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Spectator areasVent | 0.67425 | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Sports Arena Playing Area - Class I ElectricalEquipDef | NECB-B-Electric-Equipment | 2.94 | 31.6462 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Sports arena - Playing area - For a Class 1 facility | Washington State Energy Code Commercial TABLE C405.4.2Sports arena - Playing area - For a Class 1 facilityLightingDef | NECB-B-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Sports arena - court c1 | PNNL-NECB 2011DOE_PrototypeSpace Function_Sports arena - court c1Infil | Always On | Space Function | Sports arena - court c1 |  | 0.23 |  | MediumRough | 0.0216 | 3.077 | 438 | 1165 | 0.9 | 0.7 | 0.7 | Mixed_SportsArena_PlayingArea_22mm | CalculatedEstimate | PortableGoalsAndBenchesClassI |  | Mixed_SportsArena_PlayingArea_22mm | CalculatedEstimatePortableGoalsAndBenchesClassIMixed_SportsArena_PlayingArea_22mmInternalMassDef
SS Sports Arena Playing Area - Class II | 2021_WA_BuildingCode | Sports Arena | Playing Area - Class II | Sports arena - court c2 | 2021 | WA | BuildingCode | 176 | 224 | 230 | SS Sports Arena Playing Area - Class II _2021WABuildingCode | SS Sports Arena Playing Area - Class II _2021WABuildingCodeScheduleSet | 6.6667 | 150 | 1.6146 | 245 | 71.8054 | 105 | 30.7737 | 102.5791 | 97 | 120 | 0.7 | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement - Spectator areas | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Spectator areasCOMNET-REV9PeopleDef | NECB-B-Occupancy | SS Sports Arena Playing Area - Class II Activity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement - Spectator areas |  |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Spectator areasVent | 0.67425 | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Sports Arena Playing Area - Class II ElectricalEquipDef | NECB-B-Electric-Equipment | 2.01 | 21.6356 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Sports arena - Playing area - For a Class 2 facility | Washington State Energy Code Commercial TABLE C405.4.2Sports arena - Playing area - For a Class 2 facilityLightingDef | NECB-B-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Sports arena - court c2 | PNNL-NECB 2011DOE_PrototypeSpace Function_Sports arena - court c2Infil | Always On | Space Function | Sports arena - court c2 |  | 0.23 |  | MediumRough | 0.0216 | 3.077 | 438 | 1165 | 0.9 | 0.7 | 0.7 | Mixed_SportsArena_PlayingArea_22mm | CalculatedEstimate | PortableGoalsAndBenchesClassII |  | Mixed_SportsArena_PlayingArea_22mm | CalculatedEstimatePortableGoalsAndBenchesClassIIMixed_SportsArena_PlayingArea_22mmInternalMassDef
SS Sports Arena Playing Area - Class III | 2021_WA_BuildingCode | Sports Arena | Playing Area - Class III | Sports arena - court c3 | 2021 | WA | BuildingCode | 70 | 130 | 180 | SS Sports Arena Playing Area - Class III _2021WABuildingCode | SS Sports Arena Playing Area - Class III _2021WABuildingCodeScheduleSet | 6.6667 | 150 | 1.6146 | 245 | 71.8054 | 105 | 30.7737 | 102.5791 | 97 | 120 | 0.7 | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement - Spectator areas | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Spectator areasCOMNET-REV9PeopleDef | NECB-B-Occupancy | SS Sports Arena Playing Area - Class III Activity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement - Spectator areas |  |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Spectator areasVent | 0.67425 | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Sports Arena Playing Area - Class III ElectricalEquipDef | NECB-B-Electric-Equipment | 1.3 | 13.9932 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Sports arena - Playing area - For a Class 3 facility | Washington State Energy Code Commercial TABLE C405.4.2Sports arena - Playing area - For a Class 3 facilityLightingDef | NECB-B-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Sports arena - court c3 | PNNL-NECB 2011DOE_PrototypeSpace Function_Sports arena - court c3Infil | Always On | Space Function | Sports arena - court c3 |  | 0.23 |  | MediumRough | 0.0216 | 3.077 | 438 | 1165 | 0.9 | 0.7 | 0.7 | Mixed_SportsArena_PlayingArea_22mm | CalculatedEstimate | PortableGoalsAndBenchesClassIII |  | Mixed_SportsArena_PlayingArea_22mm | CalculatedEstimatePortableGoalsAndBenchesClassIIIMixed_SportsArena_PlayingArea_22mmInternalMassDef
SS Sports Arena Playing Area - Class IV | 2021_WA_BuildingCode | Sports Arena | Playing Area - Class IV | Sports arena - court c4 | 2021 | WA | BuildingCode | 0 | 191 | 255 | SS Sports Arena Playing Area - Class IV_2021WABuildingCode | SS Sports Arena Playing Area - Class IV_2021WABuildingCodeScheduleSet | 6.6667 | 150 | 1.6146 | 245 | 71.8054 | 105 | 30.7737 | 102.5791 | 97 | 120 | 0.7 | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement - Spectator areas | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Spectator areasCOMNET-REV9PeopleDef | NECB-B-Occupancy | SS Sports Arena Playing Area - Class IVActivity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Sports and amusement - Spectator areas |  |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Spectator areasVent | 0.67425 | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Sports Arena Playing Area - Class IVElectricalEquipDef | NECB-B-Electric-Equipment | 0.86 | 9.257 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Sports arena - Playing area - For a Class 4 facility | Washington State Energy Code Commercial TABLE C405.4.2Sports arena - Playing area - For a Class 4 facilityLightingDef | NECB-B-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Sports arena - court c4 | PNNL-NECB 2011DOE_PrototypeSpace Function_Sports arena - court c4Infil | Always On | Space Function | Sports arena - court c4 |  | 0.23 |  | MediumRough | 0.0216 | 3.077 | 438 | 1165 | 0.9 | 0.7 | 0.7 | Mixed_SportsArena_PlayingArea_22mm | CalculatedEstimate | PortableGoalsAndBenchesClassIV |  | Mixed_SportsArena_PlayingArea_22mm | CalculatedEstimatePortableGoalsAndBenchesClassIVMixed_SportsArena_PlayingArea_22mmInternalMassDef
SS Transportation - Baggage/Carousel Area | 2021_WA_BuildingCode | Transportation Facility | Baggage/Carousel Area | Transp. baggage | 2021 | WA | BuildingCode | 135 | 206 | 250 | SS Transportation - Baggage/Carousel Area _2021WABuildingCode | SS Transportation - Baggage/Carousel Area _2021WABuildingCodeScheduleSet | 10 | 100 | 1.0764 | 225 | 65.9437 | 105 | 30.7737 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1 | Transportation - Transportation waiting | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Transportation - Transportation waitingCOMNET-REV9PeopleDef | NECB-H-Occupancy | SS Transportation - Baggage/Carousel Area Activity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Transportation - Transportation waiting |  |  | Washington State Mechanical Code TABLE 403.3.1.1Transportation - Transportation waitingVent | 0.76225 | 8.2048 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Transportation - Baggage/Carousel Area ElectricalEquipDef | NECB-H-Electric-Equipment | 0.39 | 4.198 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Transportation - In a baggage/carousel area | Washington State Energy Code Commercial TABLE C405.4.2Transportation - In a baggage/carousel areaLightingDef | NECB-H-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Transp. baggage | PNNL-NECB 2011DOE_PrototypeSpace Function_Transp. baggageInfil | Always On | Space Function | Transp. baggage |  | 0.98 |  | MediumRough | 0.0045 | 37.62 | 3363 | 670 | 0.9 | 0.7 | 0.7 | Mixed_Transportation_BaggageCarousel_5mm | CalculatedEstimate | CarouselsAndBaggageCarts |  | Mixed_Transportation_BaggageCarousel_5mm | CalculatedEstimateCarouselsAndBaggageCartsMixed_Transportation_BaggageCarousel_5mmInternalMassDef
SS Transportation - Concourse | 2021_WA_BuildingCode | Transportation Facility | Concourse | Transp. concourse | 2021 | WA | BuildingCode | 138 | 43 | 226 | SS Transportation - Concourse_2021WABuildingCode | SS Transportation - Concourse_2021WABuildingCodeScheduleSet | 10 | 100 | 1.0764 | 225 | 65.9437 | 105 | 30.7737 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1 | Transportation - Transportation waiting | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Transportation - Transportation waitingCOMNET-REV9PeopleDef | NECB-H-Occupancy | SS Transportation - ConcourseActivity | 7.5 | 0.0035394 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Transportation - Transportation waiting |  |  | Washington State Mechanical Code TABLE 403.3.1.1Transportation - Transportation waitingVent | 0.76225 | 8.2048 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Transportation - ConcourseElectricalEquipDef | NECB-H-Electric-Equipment | 0.25 | 2.691 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Transportation - In an airport concourse | Washington State Energy Code Commercial TABLE C405.4.2Transportation - In an airport concourseLightingDef | NECB-H-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Transp. concourse | PNNL-NECB 2011DOE_PrototypeSpace Function_Transp. concourseInfil | Always On | Space Function | Transp. concourse |  | 0.37 |  | MediumRough | 0.005 | 35.72 | 2081 | 857 | 0.9 | 0.7 | 0.7 | Mixed_Transportation_Concourse_5mm | CalculatedEstimate | GateSeatingKiosksAndWalkway |  | Mixed_Transportation_Concourse_5mm | CalculatedEstimateGateSeatingKiosksAndWalkwayMixed_Transportation_Concourse_5mmInternalMassDef
SS Transportation - Ticket Counter | 2021_WA_BuildingCode | Transportation Facility | Ticket Counter | Transp. counter | 2021 | WA | BuildingCode | 32 | 178 | 170 | SS Transportation - Ticket Counter_2021WABuildingCode | SS Transportation - Ticket Counter_2021WABuildingCodeScheduleSet | 16.6667 | 60 | 0.64583 | 225 | 65.9437 | 105 | 30.7737 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1 | Theaters - Ticket booths | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Theaters - Ticket boothsCOMNET-REV9PeopleDef | NECB-H-Occupancy | SS Transportation - Ticket CounterActivity | 5 | 0.0023596 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Theaters - Ticket booths |  |  | Washington State Mechanical Code TABLE 403.3.1.1Theaters - Ticket boothsVent | 0.76225 | 8.2048 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Transportation - Ticket CounterElectricalEquipDef | NECB-H-Electric-Equipment | 0.51 | 5.4896 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Transportation - At a terminal ticket counter | Washington State Energy Code Commercial TABLE C405.4.2Transportation - At a terminal ticket counterLightingDef | NECB-H-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Transp. counter | PNNL-NECB 2011DOE_PrototypeSpace Function_Transp. counterInfil | Always On | Space Function | Transp. counter |  | 1.07 |  | MediumRough | 0.0105 | 5.172 | 1374 | 952 | 0.9 | 0.7 | 0.7 | Mixed_Transportation_TicketCounter_11mm | CalculatedEstimate | GraniteCountersAndQueueStanchions |  | Mixed_Transportation_TicketCounter_11mm | CalculatedEstimateGraniteCountersAndQueueStanchionsMixed_Transportation_TicketCounter_11mmInternalMassDef
SS Warehouse - Medium/Bulky Items on Pallets | 2021_WA_BuildingCode | Warehouse | Medium/Bulky Items on Pallets | Warehouse - med/blk | 2021 | WA | BuildingCode | 220 | 20 | 60 | SS Warehouse - Medium/Bulky Items on Pallets_2021WABuildingCode | SS Warehouse - Medium/Bulky Items on Pallets_2021WABuildingCodeScheduleSet | [18 empty] | 10 | 0.0047192 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Retail stores, sales floors, and showroom floors - Warehouses (see Storage) |  |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Warehouses (see Storage)Vent | 0.31395 | 3.3793 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Warehouse - Medium/Bulky Items on PalletsElectricalEquipDef | NECB-A-Electric-Equipment | 0.33 | 3.5521 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Warehouse - Storage area - For medium to bulky palletized items | Washington State Energy Code Commercial TABLE C405.4.2Warehouse - Storage area - For medium to bulky palletized itemsLightingDef | NECB-A-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Warehouse - med/blk | PNNL-NECB 2011DOE_PrototypeSpace Function_Warehouse - med/blkInfil | Always On | Space Function | Warehouse - med/blk |  | 1.15 |  | MediumRough | 0.0464 | 2.789 | 1088 | 1158 | 0.9 | 0.7 | 0.7 | Mixed_Warehouse_PalletItems_46mm | CalculatedEstimate | PalletRackingAndStoredGoods |  | Mixed_Warehouse_PalletItems_46mm | CalculatedEstimatePalletRackingAndStoredGoodsMixed_Warehouse_PalletItems_46mmInternalMassDef
SS Warehouse - Smaller Hand Carried Items | 2021_WA_BuildingCode | Warehouse | Smaller Hand Carried Items | Warehouse - fine | 2021 | WA | BuildingCode | 255 | 160 | 122 | SS Warehouse - Smaller Hand Carried Items_2021WABuildingCode | SS Warehouse - Smaller Hand Carried Items_2021WABuildingCodeScheduleSet | [18 empty] | 10 | 0.0047192 | 0.06 | 0.0003048 |  |  |  | Washington State Mechanical Code TABLE 403.3.1.1 | Retail stores, sales floors, and showroom floors - Warehouses (see Storage) |  |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Warehouses (see Storage)Vent | 0.31395 | 3.3793 | 0 | 0.5 | 0 | COMNET-REV9 |  | DOEPrototype | COMNET-REV9DOEPrototypeSS Warehouse - Smaller Hand Carried ItemsElectricalEquipDef | NECB-A-Electric-Equipment | 0.69 | 7.4272 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Warehouse - Storage area - For smaller, hand-carried items | Washington State Energy Code Commercial TABLE C405.4.2Warehouse - Storage area - For smaller, hand-carried itemsLightingDef | NECB-A-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Warehouse - fine | PNNL-NECB 2011DOE_PrototypeSpace Function_Warehouse - fineInfil | Always On | Space Function | Warehouse - fine |  | 1.92 |  | MediumRough | 0.0101 | 4.073 | 1303 | 1027 | 0.9 | 0.7 | 0.7 | Mixed_Warehouse_HandCarryItems_10mm | CalculatedEstimate | BoltlessShelvingAndBinStorage |  | Mixed_Warehouse_HandCarryItems_10mm | CalculatedEstimateBoltlessShelvingAndBinStorageMixed_Warehouse_HandCarryItems_10mmInternalMassDef
CS Food Preparation - Electric Cooking | 2021_WA_BuildingCode | Commercial Kitchen | Food Preparation - Electric Cooking | Food preparation | 2021 | WA | BuildingCode | 255 | 178 | 102 | CS Food Preparation - Electric Cooking_2021WABuildingCode | CS Food Preparation - Electric Cooking_2021WABuildingCodeScheduleSet | 50 | 20 | 0.21528 | 275 | 80.5979 | 275 | 80.5979 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1 | Food and beverage service_Kitchens (cooking) | COMNET-REV9 |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Kitchens (cooking)COMNET-REV9PeopleDef | NECB-B-Occupancy | CS Food Preparation - Electric CookingActivity | 7.5 | 0.0035394 | 0.12 | 0.0006096 | 0.7 | 0.00033036 |  | Washington State Mechanical Code TABLE 403.3.1.1 | Food and beverage service_Kitchens (cooking) |  |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Kitchens (cooking)Vent | 10.278 | 110.6324 | 0.25 | 0.3 | 0.2 | COMNET-REV9 | California Commercial End-Use Survey (CEUS) | DOEPrototype | COMNET-REV9California Commercial End-Use Survey (CEUS)DOEPrototypeCS Food Preparation - Electric CookingElectricalEquipDef | NECB-B-Electric-Equipment | 1.09 | 11.7328 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2 |  | Food preparation | Washington State Energy Code Commercial TABLE C405.4.2Food preparationLightingDef | NECB-B-Lighting | [11 empty] | 0.049225 |  | 2.3232e-05 | PNNL- | NECB 2011 | DOE_Prototype | Space Function_Food preparation | PNNL-NECB 2011DOE_PrototypeSpace Function_Food preparationInfil | Always On | Space Function | Food preparation |  | 1.6 |  | MediumRough | 0.0063 | 16.8 | 2640 | 512 | 0.9 | 0.7 | 0.7 | Mixed_FoodPrep_ElectricCooking_6mm | CalculatedEstimate | CommercialKitchenEquipmentSameAsGasCooking |  | Mixed_FoodPrep_ElectricCooking_6mm | CalculatedEstimateCommercialKitchenEquipmentSameAsGasCookingMixed_FoodPrep_ElectricCooking_6mmInternalMassDef
Note on U2: Mike Lovejoy: Generated schedule is constant.
Note on V2: Mike Lovejoy: Generated schedule is constant.
Note on W2: Mike Lovejoy: Generated schedule is constant.
Note on Q3: Charles Eley: Source SSPC 90.1 Envelope Trade-off Rules
Note on AR3: Source: NREL 956 and Eley Analysis. See separate spreadsheet and documentation.
Note on BB3: Source: NREL 956 and Eley Analysis. See separate spreadsheet and documentation.
Note on BK3: Source: CEUS

## ExportToCSV
d83d8e85-c973-43f1-8010-e8f36dc62725 | 464b7a91-abc0-48af-b607-07922fa703df | 789d7a7f-91a3-4dde-9310-9a74c14d32e5 | c3101f12-7b66-41ad-90b5-0c5afec65227 | bb3bf4f1-c80b-43b9-93a6-263313c59141 | f48c2a4a-3151-4163-b625-b93c6c227f62 | 35292a8f-2c31-428e-b12b-ecb42e41f30c | c318426a-e0cf-4c00-830e-9470f81507bb | 36715673-fabf-4b26-bcb3-54efccbcf6ca | 1f550d2e-d956-4855-8f6c-850193633ba2 | f70f21e0-e825-4f34-a3a0-3417ba47b289 | 0a44a70a-025f-4b95-b067-1905cd773228 | f3e926b6-9054-43e5-b214-72715fea5476 | 7e5f790a-2539-4f59-b04d-75858ff1caa0 | 0e52365f-0968-4865-98c8-5a391db72fe1 | 729982cd-0e35-4f56-90dd-aa3ce52c45a4 | 7c329b17-a9b9-429d-87d6-8d696bb1a0f1 | a791e0a0-108f-4ea5-ac55-ffbc9ef41f04 | 03d16ff5-015b-4c1f-89e1-fb9e8f3c323e | 41dd9f25-8df0-46e6-9f29-cceef9210ae8 | f8a27cd2-f746-4301-a112-59d13e40d78d | dd740279-a043-472e-9440-1247838bdebd | 93c3190c-58c6-4fa6-b31d-e972f017b622 | e7668a0e-eeeb-49fe-b68d-e4673ff0492f | 17a128c0-8bb3-42fe-8fa8-e9b6c9857c61 | 88a913cc-2e7a-402c-8f68-e04d9aea2bfe | 922e17af-4f99-4a08-92d5-c8797f685f91 | da106b8e-74c8-48ae-9585-c42116b2ba37 | 37274c8e-ef2a-4273-be16-1568ef1010d8 | 2f6014cb-8ffd-48ef-8c06-e2f22e8f09fb | 8cd22776-3059-4312-be9f-414a4cc9a5d4 | 06a4bb43-86fe-4d0d-b323-df7f797ddedf | 75657b05-6269-49ed-9dde-0685e47cd2e8 | d7a052b3-0fd2-4248-aceb-14699019a4a4 | fa38e540-d001-49d9-b3f1-d1a707fc1579 | 297cff0e-3751-4d1e-8c51-b492f8bae160 | 4478951e-a465-46c5-913d-bcea7a66cb2a | be6b6705-67ab-46ec-a6e5-80adf6c48c0a | 821df950-1005-42a1-bb71-94e21d06f843 | f0b3db32-813a-495e-9ca0-dde8056737c8 | 94e29b50-ba90-424a-98b8-c2dc37ad1d28 | 620be5d0-583e-43e9-b3de-0b70c7cf5176 | 953b161f-1acf-4fc3-a393-bdce6b3c5153 | b80aad76-63a0-4cbf-802e-5e89b172c4f9 | 1bd0cfbf-ead3-4e72-b15b-e4980f9b59db | dc1f4078-c6b5-4ccb-a537-4da64d413107 | cff5961c-e380-4d30-9a4d-0bfdf353115f | 5a6d7588-d7ab-4a8a-be29-d0e69477a2d9 | 51ff4529-089d-43c6-90c4-e6bdcb13b9fe | dc5451c6-9cf1-4680-bb77-8c264cd2f1ec | 50e1157d-9579-4ef9-b50e-099cefad7e0f | 2810bb86-71f1-4ece-94e6-b7427b2274ef | feb23d72-7ec3-4505-84ec-987e02009258 | 65c47774-d0bf-4ce9-ba77-1b1304459dc7
BA Automotive Facility | 2021_WA_BuildingCode | Automotive Facility | Whole Building | 255 | 255 | 255 | BA Automotive Facility_2021WABuildingCode | BA Automotive Facility_2021WABuildingCodeScheduleSet | 0.075272 | 293.0832 | 97 | 120 | 0.375 | COMNET-REV9WholeBuildingBA Automotive FacilityPeopleDef | NECB-E-Occupancy | BA Automotive FacilityActivity |  | 0.00127 |  | COMNET-REV9WholeBuildingBA Automotive FacilityVent | 5.417 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Automotive FacilityElectricalEquipDef | NECB-E-Electric-Equipment | 6.889 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Automotive facilityLightingDef | NECB-E-Lighting | 8.1099 | 0 | 0.75 | 0.25 | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Automotive FacilityGasEquipDef | NECB-E-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA Automotive FacilityInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Convention Center | 2021_WA_BuildingCode | Convention Center | Whole Building | 255 | 255 | 255 | BA Convention Center_2021WABuildingCode | BA Convention Center_2021WABuildingCodeScheduleSet | 0.5382 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA Convention CenterPeopleDef | NECB-C-Occupancy | BA Convention CenterActivity |  | 0.0015748 |  | COMNET-REV9WholeBuildingBA Convention CenterVent | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Convention CenterElectricalEquipDef | NECB-C-Electric-Equipment | 6.889 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Convention centerLightingDef | NECB-C-Lighting | 0.24575 | 0 | 0.75 | 0.25 | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Convention CenterGasEquipDef | NECB-C-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA Convention CenterInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Courthouse | 2021_WA_BuildingCode | Courthouse | Whole Building | 255 | 255 | 255 | BA Courthouse_2021WABuildingCode | BA Courthouse_2021WABuildingCodeScheduleSet | 0.76885 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA CourthousePeopleDef | NECB-A-Occupancy | BA CourthouseActivity |  | 0.0020828 |  | COMNET-REV9WholeBuildingBA CourthouseVent | 17.9649 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA CourthouseElectricalEquipDef | NECB-A-Electric-Equipment | 8.5036 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Court houseLightingDef | NECB-A-Lighting | 1.8432 | 0.01 | 0.4 | 0.4 | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA CourthouseGasEquipDef | NECB-A-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA CourthouseInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Dining: Bar Lounge/Leisure | 2021_WA_BuildingCode | Dining: Bar Lounge/Leisure | Whole Building | 255 | 255 | 255 | BA Dining: Bar Lounge/Leisure_2021WABuildingCode | BA Dining: Bar Lounge/Leisure_2021WABuildingCodeScheduleSet | 1.0764 | 161.1958 | 97 | 120 | 0.5 | COMNET-REV9WholeBuildingBA Dining: Bar Lounge/LeisurePeopleDef | NECB-B-Occupancy | BA Dining: Bar Lounge/LeisureActivity |  | 0.0047244 |  | COMNET-REV9WholeBuildingBA Dining: Bar Lounge/LeisureVent | 14.166 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Dining: Bar Lounge/LeisureElectricalEquipDef | NECB-B-Electric-Equipment | 8.5036 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Dining: Bar lounge/leisureLightingDef | NECB-B-Lighting | 188.7386 | 0 | 0.75 | 0.25 | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Dining: Bar Lounge/LeisureGasEquipDef | RestaurantFastFood BLDG_EQUIP_SCH | 2.3232e-05 | PNNL-NECB 2011BA Dining: Bar Lounge/LeisureInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Dining: Cafeteria/Fast Food | 2021_WA_BuildingCode | Dining: Cafeteria/Fast Food | Whole Building | 255 | 255 | 255 | BA Dining: Cafeteria/Fast Food_2021WABuildingCode | BA Dining: Cafeteria/Fast Food_2021WABuildingCodeScheduleSet | 1.0764 | 161.1958 | 97 | 120 | 0.5 | COMNET-REV9WholeBuildingBA Dining: Cafeteria/Fast FoodPeopleDef | NECB-B-Occupancy | BA Dining: Cafeteria/Fast FoodActivity |  | 0.0047244 |  | COMNET-REV9WholeBuildingBA Dining: Cafeteria/Fast FoodVent | 14.729 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Dining: Cafeteria/Fast FoodElectricalEquipDef | NECB-B-Electric-Equipment | 7.7501 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Dining: Cafeteria/fast foodLightingDef | NECB-B-Lighting | 188.7386 | 0 | 0.75 | 0.25 | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Dining: Cafeteria/Fast FoodGasEquipDef | RestaurantFastFood BLDG_EQUIP_SCH | 2.3232e-05 | PNNL-NECB 2011BA Dining: Cafeteria/Fast FoodInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Dining: Family | 2021_WA_BuildingCode | Dining: Family | Whole Building | 255 | 255 | 255 | BA Dining: Family_2021WABuildingCode | BA Dining: Family_2021WABuildingCodeScheduleSet | 0.76885 | 161.1958 | 97 | 120 | 0.5 | COMNET-REV9WholeBuildingBA Dining: FamilyPeopleDef | NECB-B-Occupancy | BA Dining: FamilyActivity |  | 0.0036068 |  | COMNET-REV9WholeBuildingBA Dining: FamilyVent | 13.5949 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Dining: FamilyElectricalEquipDef | NECB-B-Electric-Equipment | 7.6424 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Dining: FamilyLightingDef | NECB-B-Lighting | 188.7386 | 0.05 | 0.4 | 0.4 | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA Dining: FamilyGasEquipDef | RestaurantSitDown BLDG_EQUIP_SCH | 2.3232e-05 | PNNL-NECB 2011BA Dining: FamilyInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Dormitory | 2021_WA_BuildingCode | Dormitory | Whole Building | 255 | 255 | 255 | BA Dormitory_2021WABuildingCode | BA Dormitory_2021WABuildingCodeScheduleSet | 0.10764 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA DormitoryPeopleDef | NECB-G-Occupancy | BA DormitoryActivity |  | 0.0005588 |  | COMNET-REV9WholeBuildingBA DormitoryVent | 21.0558 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA DormitoryElectricalEquipDef | NECB-G-Electric-Equipment | 4.9514 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2DormitoryLightingDef | NECB-G-Lighting | 7.4955 | 0.01 | 0.4 | 0.4 | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA DormitoryGasEquipDef | ApartmentMidRise EQP_APT_SCH | 2.3232e-05 | PNNL-NECB 2011BA DormitoryInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Exercise Center | 2021_WA_BuildingCode | Exercise Center | Whole Building | 255 | 255 | 255 | BA Exercise Center_2021WABuildingCode | BA Exercise Center_2021WABuildingCodeScheduleSet | 0.10764 | 527.5498 | 97 | 120 | 0.39444 | COMNET-REV9WholeBuildingBA Exercise CenterPeopleDef | NECB-B-Occupancy | BA Exercise CenterActivity |  | 0.0013208 |  | COMNET-REV9WholeBuildingBA Exercise CenterVent | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Exercise CenterElectricalEquipDef | NECB-B-Electric-Equipment | 7.2119 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Exercise centerLightingDef | NECB-B-Lighting | 0.24575 | 0.05 | 0.4 | 0.4 | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA Exercise CenterGasEquipDef | HotelSmall ExerciseCenter_Eqp_Sch | 2.3232e-05 | PNNL-NECB 2011BA Exercise CenterInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Fire Station | 2021_WA_BuildingCode | Fire Station | Whole Building | 255 | 255 | 255 | BA Fire Station_2021WABuildingCode | BA Fire Station_2021WABuildingCodeScheduleSet | 0.32618 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA Fire StationPeopleDef | NECB-F-Occupancy | BA Fire StationActivity |  | 0.0010668 |  | COMNET-REV9WholeBuildingBA Fire StationVent | 16.5804 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Fire StationElectricalEquipDef | NECB-F-Electric-Equipment | 5.8126 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Fire stationLightingDef | NECB-F-Lighting | 8.1099 | 0 | 0.75 | 0.25 | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Fire StationGasEquipDef | NECB-F-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA Fire StationInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Gymnasium | 2021_WA_BuildingCode | Gymnasium | Whole Building | 255 | 255 | 255 | BA Gymnasium_2021WABuildingCode | BA Gymnasium_2021WABuildingCodeScheduleSet | 0.32618 | 527.5498 | 97 | 120 | 0.39444 | COMNET-REV9WholeBuildingBA GymnasiumPeopleDef | NECB-B-Occupancy | BA GymnasiumActivity |  | 0.001524 |  | COMNET-REV9WholeBuildingBA GymnasiumVent | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA GymnasiumElectricalEquipDef | NECB-B-Electric-Equipment | 8.073 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2GymnasiumLightingDef | NECB-B-Lighting | 0.24575 | 0 | 0.75 | 0.25 | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA GymnasiumGasEquipDef | SchoolSecondary BLDG_EQUIP_SCH | 2.3232e-05 | PNNL-NECB 2011BA GymnasiumInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Healthcare Clinic | 2021_WA_BuildingCode | Healthcare Clinic | Whole Building | 255 | 255 | 255 | BA Healthcare Clinic_2021WABuildingCode | BA Healthcare Clinic_2021WABuildingCodeScheduleSet | 0.05382 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA Healthcare ClinicPeopleDef | NECB-A-Occupancy | BA Healthcare ClinicActivity |  | 0.0023876 |  | COMNET-REV9WholeBuildingBA Healthcare ClinicVent | 13.1339 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Healthcare ClinicElectricalEquipDef | NECB-A-Electric-Equipment | 7.5348 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Health care clinicLightingDef | NECB-A-Lighting | 12.1648 | 0 | 0 | 0.5 | COMNET-REV9California Commercial End-Use Survey (CEUS)DOEPrototypeBA Healthcare ClinicGasEquipDef | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | 2.3232e-05 | PNNL-NECB 2011BA Healthcare ClinicInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Hospital | 2021_WA_BuildingCode | Hospital | Whole Building | 255 | 255 | 255 | BA Hospital_2021WABuildingCode | BA Hospital_2021WABuildingCodeScheduleSet | 0.05382 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA HospitalPeopleDef | NECB-H-Occupancy | BA HospitalActivity |  | 0.0023876 |  | COMNET-REV9WholeBuildingBA HospitalVent | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA HospitalElectricalEquipDef | NECB-H-Electric-Equipment | 9.0418 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2HospitalLightingDef | NECB-H-Lighting | 12.1648 | 0.01 | 0.2 | 0.7 | COMNET-REV9California Commercial End-Use Survey (CEUS)DOEPrototypeBA HospitalGasEquipDef | Hospital BLDG_EQUIP_SCH | 2.3232e-05 | PNNL-NECB 2011BA HospitalInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Hotel | 2021_WA_BuildingCode | Hotel | Whole Building | 255 | 255 | 255 | BA Hotel_2021WABuildingCode | BA Hotel_2021WABuildingCodeScheduleSet | 0.043056 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA HotelPeopleDef | NECB-F-Occupancy | BA HotelActivity |  | 0.0004064 |  | COMNET-REV9WholeBuildingBA HotelVent | 16.8363 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA HotelElectricalEquipDef | NECB-F-Electric-Equipment | 6.0278 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2HotelLightingDef | NECB-F-Lighting | 7.4955 | 0 | 0.5 | 0 | COMNET-REV9California Commercial End-Use Survey (CEUS)DOEPrototypeBA HotelGasEquipDef | HotelLarge BLDG_EQUIP_SCH | 2.3232e-05 | PNNL-NECB 2011BA HotelInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Library | 2021_WA_BuildingCode | Library | Whole Building | 255 | 255 | 255 | BA Library_2021WABuildingCode | BA Library_2021WABuildingCodeScheduleSet | 0.10764 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA LibraryPeopleDef | NECB-C-Occupancy | BA LibraryActivity |  | 0.0005588 |  | COMNET-REV9WholeBuildingBA LibraryVent | 10.0883 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA LibraryElectricalEquipDef | NECB-C-Electric-Equipment | 8.9341 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2LibraryLightingDef | NECB-C-Lighting | 0.24575 | 0.01 | 0.4 | 0.4 | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA LibraryGasEquipDef | NECB-C-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA LibraryInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Manufacturing Facility | 2021_WA_BuildingCode | Manufacturing Facility | Whole Building | 255 | 255 | 255 | BA Manufacturing Facility_2021WABuildingCode | BA Manufacturing Facility_2021WABuildingCodeScheduleSet | 0.075272 | 424.9707 | 97 | 120 | 0.4 | COMNET-REV9WholeBuildingBA Manufacturing FacilityPeopleDef | NECB-A-Occupancy | BA Manufacturing FacilityActivity |  | 0.00127 |  | COMNET-REV9WholeBuildingBA Manufacturing FacilityVent | 3.7116 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Manufacturing FacilityElectricalEquipDef | NECB-A-Electric-Equipment | 8.8265 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Manufacturing facilityLightingDef | NECB-A-Lighting | 8.1099 | 0 | 0.75 | 0.25 | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Manufacturing FacilityGasEquipDef | NECB-A-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA Manufacturing FacilityInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Motel | 2021_WA_BuildingCode | Motel | Whole Building | 255 | 255 | 255 | BA Motel_2021WABuildingCode | BA Motel_2021WABuildingCodeScheduleSet | 0.043056 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA MotelPeopleDef | NECB-F-Occupancy | BA MotelActivity |  | 0.0004064 |  | COMNET-REV9WholeBuildingBA MotelVent | 16.8363 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA MotelElectricalEquipDef | NECB-F-Electric-Equipment | 6.0278 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2HotelLightingDef | NECB-F-Lighting | 7.4955 | 0.01 | 0.4 | 0.4 | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA MotelGasEquipDef | NECB-F-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA MotelInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Motion Picture Theater | 2021_WA_BuildingCode | Motion Picture Theater | Whole Building | 255 | 255 | 255 | BA Motion Picture Theater_2021WABuildingCode | BA Motion Picture Theater_2021WABuildingCodeScheduleSet | 1.5377 | 96.7175 | 97 | 120 | 0.68182 | COMNET-REV9WholeBuildingBA Motion Picture TheaterPeopleDef | NECB-C-Occupancy | BA Motion Picture TheaterActivity |  | 0.0060452 |  | COMNET-REV9WholeBuildingBA Motion Picture TheaterVent | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Motion Picture TheaterElectricalEquipDef | NECB-C-Electric-Equipment | 4.7362 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Motion picture theaterLightingDef | NECB-C-Lighting | 0.24575 | 0.01 | 0.4 | 0.4 | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA Motion Picture TheaterGasEquipDef | NECB-C-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA Motion Picture TheaterInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Multifamily | 2021_WA_BuildingCode | Multifamily | Whole Building | 255 | 255 | 255 | BA Multifamily_2021WABuildingCode | BA Multifamily_2021WABuildingCodeScheduleSet | 0.028326 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA MultifamilyPeopleDef | NECB-G-Occupancy | BA MultifamilyActivity |  | 0.0003048 |  | COMNET-REV9WholeBuildingBA MultifamilyVent | 15.3331 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA MultifamilyElectricalEquipDef | NECB-G-Electric-Equipment | 4.4132 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Multiple familyLightingDef | NECB-G-Lighting | 7.4955 | 0.01 | 0.4 | 0.4 | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA MultifamilyGasEquipDef | NECB-G-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA MultifamilyInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Museum | 2021_WA_BuildingCode | Museum | Whole Building | 255 | 255 | 255 | BA Museum_2021WABuildingCode | BA Museum_2021WABuildingCodeScheduleSet | 0.43056 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA MuseumPeopleDef | NECB-C-Occupancy | BA MuseumActivity |  | 0.0018288 |  | COMNET-REV9WholeBuildingBA MuseumVent | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA MuseumElectricalEquipDef | NECB-C-Electric-Equipment | 5.9202 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2MuseumLightingDef | NECB-C-Lighting | 0.24575 | 0 | 0.75 | 0.25 | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA MuseumGasEquipDef | NECB-A-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA MuseumInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Office | 2021_WA_BuildingCode | Office | Whole Building | 255 | 255 | 255 | BA Office_2021WABuildingCode | BA Office_2021WABuildingCodeScheduleSet | 0.05382 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA OfficePeopleDef | NECB-A-Occupancy | BA OfficeActivity |  | 0.0004572 |  | COMNET-REV9WholeBuildingBA OfficeVent | 17.9987 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA OfficeElectricalEquipDef | NECB-A-Electric-Equipment | 6.889 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2OfficeLightingDef | NECB-A-Lighting | 1.3516 | 0.01 | 0.4 | 0.4 | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA OfficeGasEquipDef | OfficeMedium BLDG_EQUIP_SCH | 2.3232e-05 | PNNL-NECB 2011BA OfficeInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Parking Garage | 2021_WA_BuildingCode | Parking Garage | Whole Building | 255 | 255 | 255 | BA Parking Garage_2021WABuildingCode | BA Parking Garage_2021WABuildingCodeScheduleSet | [12 empty] | 3.2292 | 0 | 0.06 | 0.88 | Medium Estimate: Workplace, 20% of Spaces with Level 2 Charger12%lost to heatDOEPrototypeBA Parking GarageElectricalEquipDef | NECB-H-Electric-Equipment | 1.507 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Parking garageLightingDef | NECB-H-Lighting | 0 | 0 | 0.75 | 0.25 | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Parking GarageGasEquipDef | NECB-H-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA Parking GarageInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Penitentiary | 2021_WA_BuildingCode | Penitentiary | Whole Building | 255 | 255 | 255 | BA Penitentiary_2021WABuildingCode | BA Penitentiary_2021WABuildingCodeScheduleSet | 0.2691 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA PenitentiaryPeopleDef | NECB-H-Occupancy | BA PenitentiaryActivity |  | 0.00127 |  | COMNET-REV9WholeBuildingBA PenitentiaryVent | 16.0688 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA PenitentiaryElectricalEquipDef | NECB-H-Electric-Equipment | 6.9966 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2PenitentiaryLightingDef | NECB-H-Lighting | 7.4955 | 0 | 0.75 | 0.25 | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA PenitentiaryGasEquipDef | NECB-D-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA PenitentiaryInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Performing Arts Theater | 2021_WA_BuildingCode | Performing Arts Theater | Whole Building | 255 | 255 | 255 | BA Performing Arts Theater_2021WABuildingCode | BA Performing Arts Theater_2021WABuildingCodeScheduleSet | 0.76885 | 96.7175 | 97 | 120 | 0.68182 | COMNET-REV9WholeBuildingBA Performing Arts TheaterPeopleDef | NECB-C-Occupancy | BA Performing Arts TheaterActivity |  | 0.0038608 |  | COMNET-REV9WholeBuildingBA Performing Arts TheaterVent | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Performing Arts TheaterElectricalEquipDef | NECB-C-Electric-Equipment | 9.0418 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Performing arts theaterLightingDef | NECB-C-Lighting | 0.24575 | 0.01 | 0.4 | 0.4 | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA Performing Arts TheaterGasEquipDef | NECB-C-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA Performing Arts TheaterInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Police Station | 2021_WA_BuildingCode | Police Station | Whole Building | 255 | 255 | 255 | BA Police Station_2021WABuildingCode | BA Police Station_2021WABuildingCodeScheduleSet | 0.32618 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA Police StationPeopleDef | NECB-H-Occupancy | BA Police StationActivity |  | 0.0010668 |  | COMNET-REV9WholeBuildingBA Police StationVent | 16.5804 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Police StationElectricalEquipDef | NECB-H-Electric-Equipment | 7.1042 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Police stationLightingDef | NECB-H-Lighting | 8.1099 | 0 | 0.75 | 0.25 | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Police StationGasEquipDef | NECB-H-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA Police StationInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Post Office | 2021_WA_BuildingCode | Post Office | Whole Building | 255 | 255 | 255 | BA Post Office_2021WABuildingCode | BA Post Office_2021WABuildingCodeScheduleSet | 0.32618 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA Post OfficePeopleDef | NECB-A-Occupancy | BA Post OfficeActivity |  | 0.0010668 |  | COMNET-REV9WholeBuildingBA Post OfficeVent | 9.7853 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Post OfficeElectricalEquipDef | NECB-A-Electric-Equipment | 6.9966 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Post officeLightingDef | NECB-A-Lighting | 8.1099 | 0 | 0.75 | 0.25 | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Post OfficeGasEquipDef | NECB-A-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA Post OfficeInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Religious Building | 2021_WA_BuildingCode | Religious Building | Whole Building | 255 | 255 | 255 | BA Religious Building_2021WABuildingCode | BA Religious Building_2021WABuildingCodeScheduleSet | 1.3455 | 117.2333 | 97 | 120 | 0.6125 | COMNET-REV9WholeBuildingBA Religious BuildingPeopleDef | NECB-I-Occupancy | BA Religious BuildingActivity |  | 0.0033528 |  | COMNET-REV9WholeBuildingBA Religious BuildingVent | 3.2125 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Religious BuildingElectricalEquipDef | NECB-I-Electric-Equipment | 7.2119 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Religious buildingLightingDef | NECB-I-Lighting | 0.24575 | 0.03 | 0.4 | 0.4 | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA Religious BuildingGasEquipDef | NECB-I-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA Religious BuildingInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Retail | 2021_WA_BuildingCode | Retail | Whole Building | 255 | 255 | 255 | BA Retail_2021WABuildingCode | BA Retail_2021WABuildingCodeScheduleSet | 0.16066 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA RetailPeopleDef | NECB-C-Occupancy | BA RetailActivity |  | 0.0011684 |  | COMNET-REV9WholeBuildingBA RetailVent | 7.5601 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA RetailElectricalEquipDef | NECB-C-Electric-Equipment | 9.0418 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2RetailLightingDef | NECB-C-Lighting | 0.98301 | 0.01 | 0.4 | 0.4 | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA RetailGasEquipDef | RetailStandalone BLDG_EQUIP_SCH | 2.3232e-05 | PNNL-NECB 2011BA RetailInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA School/University | 2021_WA_BuildingCode | School/University | Whole Building | 255 | 255 | 255 | BA School/University_2021WABuildingCode | BA School/University_2021WABuildingCodeScheduleSet | 0.2691 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA School/UniversityPeopleDef | NECB-D-Occupancy | BA School/UniversityActivity |  | 0.0023876 |  | COMNET-REV9WholeBuildingBA School/UniversityVent | 7.4001 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA School/UniversityElectricalEquipDef | NECB-D-Electric-Equipment | 7.5348 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2School/universityLightingDef | NECB-D-Lighting | 1.4745 | 0.01 | 0.4 | 0.4 | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA School/UniversityGasEquipDef | SchoolSecondary BLDG_EQUIP_SCH | 2.3232e-05 | PNNL-NECB 2011BA School/UniversityInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Sports Arena | 2021_WA_BuildingCode | Sports Arena | Whole Building | 255 | 255 | 255 | BA Sports Arena_2021WABuildingCode | BA Sports Arena_2021WABuildingCodeScheduleSet | [9 empty] | 0.001524 |  | COMNET-REV9WholeBuildingBA Sports ArenaVent | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Sports ArenaElectricalEquipDef | NECB-B-Electric-Equipment | 6.6737 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Sports arenaLightingDef | NECB-B-Lighting | 0.24575 | 0 | 0.75 | 0.25 | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA Sports ArenaGasEquipDef | NECB-B-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA Sports ArenaInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Town Hall | 2021_WA_BuildingCode | Town Hall | Whole Building | 255 | 255 | 255 | BA Town Hall_2021WABuildingCode | BA Town Hall_2021WABuildingCodeScheduleSet | 0.05382 | 131.8875 | 97 | 120 | 0.55556 | COMNET-REV9WholeBuildingBA Town HallPeopleDef | NECB-D-Occupancy | BA Town HallActivity |  | 0.0004572 |  | COMNET-REV9WholeBuildingBA Town HallVent | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA Town HallElectricalEquipDef | NECB-D-Electric-Equipment | 7.4272 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Town hallLightingDef | NECB-D-Lighting | 1.3516 | 0.01 | 0.4 | 0.4 | COMNET-REV9California Commercial End-Use Survey (CEUS)60%ThermEffProcessBA Town HallGasEquipDef | NECB-D-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA Town HallInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Transportation | 2021_WA_BuildingCode | Transportation | Whole Building | 255 | 255 | 255 | BA Transportation_2021WABuildingCode | BA Transportation_2021WABuildingCodeScheduleSet | 1.0764 | 96.7175 | 97 | 120 | 0.68182 | COMNET-REV9WholeBuildingBA TransportationPeopleDef | NECB-H-Occupancy | BA TransportationActivity |  | 0.0041148 |  | COMNET-REV9WholeBuildingBA TransportationVent | 5.5878 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA TransportationElectricalEquipDef | NECB-H-Electric-Equipment | 5.382 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2TransportationLightingDef | NECB-H-Lighting | 0.24575 | 0 | 0.75 | 0.25 | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA TransportationGasEquipDef | NECB-H-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA TransportationInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Warehouse | 2021_WA_BuildingCode | Warehouse | Whole Building | 255 | 255 | 255 | BA Warehouse_2021WABuildingCode | BA Warehouse_2021WABuildingCodeScheduleSet | [9 empty] | 0.0003048 |  | COMNET-REV9WholeBuildingBA WarehouseVent | 3.254 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA WarehouseElectricalEquipDef | NECB-A-Electric-Equipment | 4.3056 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2WarehouseLightingDef | NECB-A-Lighting | 0 | 0 | 0.75 | 0.25 | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA WarehouseGasEquipDef | NECB-A-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA WarehouseInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
BA Workshop | 2021_WA_BuildingCode | Workshop | Whole Building | 255 | 255 | 255 | BA Workshop_2021WABuildingCode | BA Workshop_2021WABuildingCodeScheduleSet | 0.075272 | 468.9332 | 97 | 120 | 0.39688 | COMNET-REV9WholeBuildingBA WorkshopPeopleDef | NECB-A-Occupancy | BA WorkshopActivity |  | 0.00127 |  | COMNET-REV9WholeBuildingBA WorkshopVent | 4.6106 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeBA WorkshopElectricalEquipDef | NECB-A-Electric-Equipment | 9.7952 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2WorkshopLightingDef | NECB-A-Lighting | 8.1099 | 0 | 0.75 | 0.25 | COMNET-REV9California Commercial End-Use Survey (CEUS)93%ThermEffRadiantBA WorkshopGasEquipDef | NECB-A-Electric-Equipment | 2.3232e-05 | PNNL-NECB 2011BA WorkshopInfil | Always On |  | 2 |  | MediumSmooth | 0.15 | 0.12 | 540 | 1210 | 0.9 | 0.7 | 0.7 | Std Wood 6inch | OpenStudio-Prototype-BuildingsStd Wood 6inchInternalMassDef
CS Audience Seating Area - Auditorium | 2021_WA_BuildingCode | Auditorium | Audience Seating Area | 230 | 196 | 120 | CS Audience Seating Area - Auditorium_2021WABuildingCode | CS Audience Seating Area - Auditorium_2021WABuildingCodeScheduleSet | 1.6146 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsCOMNET-REV9PeopleDef | SchoolSecondary BLDG_OCC_SCH_Auditorium | CS Audience Seating Area - AuditoriumActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsVent | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - AuditoriumElectricalEquipDef | SchoolSecondary BLDG_EQUIP_SCH | 6.566 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - In an auditoriumLightingDef | SchoolSecondary BLDG_LIGHT_SCH | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeSecondarySchool_AuditoriumInfil | SchoolSecondary INFIL_SCH_PNNL | 0 | 2.11 | 0 | MediumRough | 0.0332 | 0.966 | 219 | 859 | 0.9 | 0.65 | 0.65 | Mixed_AudienceSeating_Auditorium_33mm | CalculatedEstimateFoldingUpholsteredSeatsWithSteelPedestalsMixed_AudienceSeating_Auditorium_33mmInternalMassDef
CS Audience Seating Area - Convention Center | 2021_WA_BuildingCode | Convention Center | Audience Seating Area | 230 | 196 | 120 | CS Audience Seating Area - Convention Center_2021WABuildingCode | CS Audience Seating Area - Convention Center_2021WABuildingCodeScheduleSet | 1.6146 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsCOMNET-REV9PeopleDef | NECB-C-Occupancy | CS Audience Seating Area - Convention CenterActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsVent | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - Convention CenterElectricalEquipDef | NECB-C-Electric-Equipment | 2.4757 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - OtherwiseLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Convention centre - audienceInfil | Always On | 0 | 1.05 | 0 | MediumRough | 0.0084 | 3.73 | 636 | 562 | 0.9 | 0.7 | 0.7 | Mixed_AudienceSeating_ConventionCenter_8mm | CalculatedEstimatePortableStackingConferenceChairsMixed_AudienceSeating_ConventionCenter_8mmInternalMassDef
CS Audience Seating Area - Exercise Center | 2021_WA_BuildingCode | Exercise Center | Audience Seating Area | 230 | 196 | 120 | CS Audience Seating Area - Exercise Center_2021WABuildingCode | CS Audience Seating Area - Exercise Center_2021WABuildingCodeScheduleSet | 1.6146 | 527.5498 | 97 | 120 | 0.39444 | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement_Spectator areasCOMNET-REV9PeopleDef | NECB-B-Occupancy | CS Audience Seating Area - Exercise CenterActivity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement_Spectator areasVent | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - Exercise CenterElectricalEquipDef | NECB-B-Electric-Equipment | 2.4757 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - OtherwiseLightingDef | NECB-B-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Gym - audienceInfil | Always On | 0 | 1.03 | 0 | Smooth | 0.01 | 50 | 332 | 863 | 0.9 | 0.65 | 0.65 | Mixed_AudienceSeating_ExCtr_10mm | CalculatedEstimateRetractableAluminumBleacherSystemMixed_AudienceSeating_ExCtr_10mmInternalMassDef
CS Audience Seating Area - Gymnasium | 2021_WA_BuildingCode | Gymnasium | Audience Seating Area | 230 | 196 | 120 | CS Audience Seating Area - Gymnasium_2021WABuildingCode | CS Audience Seating Area - Gymnasium_2021WABuildingCodeScheduleSet | 1.6146 | 527.5498 | 97 | 120 | 0.39444 | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement_Spectator areasCOMNET-REV9PeopleDef | NECB-B-Occupancy | CS Audience Seating Area - GymnasiumActivity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement_Spectator areasVent | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - GymnasiumElectricalEquipDef | NECB-B-Electric-Equipment | 2.4757 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - In a gymnasiumLightingDef | NECB-B-Lighting | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeSecondarySchool_GymInfil | SchoolSecondary INFIL_SCH_PNNL | 0 | 0.71 | 0 | Smooth | 0.01 | 50 | 382 | 851 | 0.9 | 0.65 | 0.65 | Mixed_AudienceSeating_Gymnasium_10mm | CalculatedEstimateTelescopingAluminumBleacherSystemMixed_AudienceSeating_Gymnasium_10mmInternalMassDef
CS Audience Seating Area - Motion Picture Theater | 2021_WA_BuildingCode | Theater | Audience Seating Area | 230 | 196 | 120 | CS Audience Seating Area - Motion Picture Theater_2021WABuildingCode | CS Audience Seating Area - Motion Picture Theater_2021WABuildingCodeScheduleSet | 1.6146 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsCOMNET-REV9PeopleDef | NECB-C-Occupancy | CS Audience Seating Area - Motion Picture TheaterActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsVent | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - Motion Picture TheaterElectricalEquipDef | NECB-C-Electric-Equipment | 2.9063 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - In a motion picture theaterLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Audience - motion pictureInfil | Always On | 0 | 1.81 | 0 | MediumRough | 0.0341 | 0.891 | 210 | 876 | 0.9 | 0.65 | 0.65 | Mixed_AudienceSeating_MotionPictureTheater_34mm | CalculatedEstimateFixedCinemaSeatsWithCupHoldersMixed_AudienceSeating_MotionPictureTheater_34mmInternalMassDef
CS Audience Seating Area - Penitentiary | 2021_WA_BuildingCode | Penitentiary | Audience Seating Area | 230 | 196 | 120 | CS Audience Seating Area - Penitentiary_2021WABuildingCode | CS Audience Seating Area - Penitentiary_2021WABuildingCodeScheduleSet | 0.5382 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Correctional facilities_Booking_waitingCOMNET-REV9PeopleDef | NECB-C-Occupancy | CS Audience Seating Area - PenitentiaryActivity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Correctional facilities_Booking_waitingVent | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - PenitentiaryElectricalEquipDef | NECB-C-Electric-Equipment | 7.2119 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - In a penitentiaryLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Penitentiary - audienceInfil | Always On | 0 | 1.17 | 0 | MediumSmooth | 0.0013 | 50 | 7800 | 460 | 0.9 | 0.7 | 0.7 | Steel_AudienceSeating_Penitentiary_1mm | CalculatedEstimateFixedAllMetalSecuritySeatingSteel_AudienceSeating_Penitentiary_1mmInternalMassDef
CS Audience Seating Area - Performing Arts Theater | 2021_WA_BuildingCode | Theater | Audience Seating Area | 230 | 196 | 120 | CS Audience Seating Area - Performing Arts Theater_2021WABuildingCode | CS Audience Seating Area - Performing Arts Theater_2021WABuildingCodeScheduleSet | 1.6146 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsCOMNET-REV9PeopleDef | NECB-C-Occupancy | CS Audience Seating Area - Performing Arts TheaterActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsVent | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - Performing Arts TheaterElectricalEquipDef | NECB-C-Electric-Equipment | 12.4862 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - In a performing arts theaterLightingDef | NECB-C-Lighting | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeSecondarySchool_AuditoriumInfil | SchoolSecondary INFIL_SCH_PNNL | 0 | 2.06 | 0 | MediumRough | 0.0379 | 0.863 | 200 | 879 | 0.9 | 0.65 | 0.65 | Mixed_AudienceSeating_PerformingArtsTheater_38mm | CalculatedEstimateFixedUpholsteredSeatsWithAisleRailsMixed_AudienceSeating_PerformingArtsTheater_38mmInternalMassDef
CS Audience Seating Area - Religious Building | 2021_WA_BuildingCode | Religious | Audience Seating Area | 230 | 196 | 120 | CS Audience Seating Area - Religious Building_2021WABuildingCode | CS Audience Seating Area - Religious Building_2021WABuildingCodeScheduleSet | 1.6146 | 117.2333 | 97 | 120 | 0.6125 | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsCOMNET-REV9PeopleDef | NECB-I-Occupancy | CS Audience Seating Area - Religious BuildingActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Education_AuditoriumsVent | 7.8926 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - Religious BuildingElectricalEquipDef | NECB-I-Electric-Equipment | 7.7501 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - In a religious buildingLightingDef | NECB-I-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Religious - audienceInfil | Always On | 0 | 1.17 | 0 | MediumRough | 0.0182 | 1.185 | 255 | 785 | 0.9 | 0.7 | 0.7 | Mixed_AudienceSeating_ReligiousBuilding_18mm | CalculatedEstimatePaddedStackableGangedChairsMixed_AudienceSeating_ReligiousBuilding_18mmInternalMassDef
CS Audience Seating Area - Sports Arena | 2021_WA_BuildingCode | Sports arena | Audience Seating Area | 230 | 196 | 120 | CS Audience Seating Area - Sports Arena_2021WABuildingCode | CS Audience Seating Area - Sports Arena_2021WABuildingCodeScheduleSet | 1.6146 | 102.5791 | 97 | 120 | 0.7 | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement_Spectator areasCOMNET-REV9PeopleDef | NECB-B-Occupancy | CS Audience Seating Area - Sports ArenaActivity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement_Spectator areasVent | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - Sports ArenaElectricalEquipDef | NECB-B-Electric-Equipment | 3.5521 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - In a sports arenaLightingDef | NECB-B-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Sports arena - audienceInfil | Always On | 0 | 1.75 | 0 | MediumSmooth | 0.01 | 2.66 | 440 | 1401 | 0.9 | 0.65 | 0.65 | Mixed_AudienceSeating_SportsArena_10mm | CalculatedEstimateFoldDownPolypropyleneStadiumSeatsMixed_AudienceSeating_SportsArena_10mmInternalMassDef
CS Audience Seating Area - Transportation Facility | 2021_WA_BuildingCode | Transportation Facility | Audience Seating Area | 230 | 196 | 120 | CS Audience Seating Area - Transportation Facility_2021WABuildingCode | CS Audience Seating Area - Transportation Facility_2021WABuildingCodeScheduleSet | 1.0764 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1Transportation_Transportation waitingCOMNET-REV9PeopleDef | NECB-H-Occupancy | CS Audience Seating Area - Transportation FacilityActivity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Transportation_Transportation waitingVent | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - Transportation FacilityElectricalEquipDef | NECB-H-Electric-Equipment | 2.4757 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - OtherwiseLightingDef | NECB-H-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2012DOE_PrototypeSpace Function_Transp. seatingInfil | Always On | 0 | 0.66 | 0 | MediumRough | 0.01 | 3.06 | 638 | 658 | 0.9 | 0.6 | 0.6 | Mixed_AudienceSeating_Transportation_10mm | CalculatedEstimateGangedModularWaitingSeatsMixed_AudienceSeating_Transportation_10mmInternalMassDef
CS Audience Seating Area - Other | 2021_WA_BuildingCode | Miscellaneous | Audience Seating Area | 230 | 196 | 120 | CS Audience Seating Area - Other_2021WABuildingCode | CS Audience Seating Area - Other_2021WABuildingCodeScheduleSet | 1.0764 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Education_Multiuse assemblyCOMNET-REV9BA School/UniversityPeopleDef | NECB-C-Occupancy | CS Audience Seating Area - OtherActivity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Education_Multiuse assemblyVent | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Audience Seating Area - OtherElectricalEquipDef | NECB-C-Electric-Equipment | 2.4757 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Audience/seating area - Permanent - OtherwiseLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2013DOE_PrototypeSpace Function_Audience - auditoriumInfil | Always On | 0 | 1.13 | 0 | MediumRough | 0.0079 | 1.86 | 364 | 691 | 0.9 | 0.65 | 0.65 | Mixed_AudienceSeating_Other_8mm | CalculatedEstimatePortablePaddedFoldingChairsMixed_AudienceSeating_Other_8mmInternalMassDef
CS Atrium - Less than or equal to 40 ft | 2021_WA_BuildingCode | Atrium | Atrium - Less than or equal to 40 ft | 255 | 255 | 0 | CS Atrium - Less than or equal to 40 ft_2021WABuildingCode | CS Atrium - Less than or equal to 40 ft_2021WABuildingCodeScheduleSet | [9 empty] | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_Corridors other than Group RVent | [6 empty] | 5.1667 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Atrium - 20 to 40 feet in heightLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2014DOE_PrototypeSpace Function_Atrium - H < 13mInfil | Always On |  | 0.31 | 0 | MediumRough | 0.085 | 2.56 | 904 | 1122 | 0.9 | 0.7 | 0.7 | Mixed_Atrium_LTE40ft_85mm | CalculatedEstimateLightWoodTrussesOrSmallSteelBeamsMixed_Atrium_LTE40ft_85mmInternalMassDef
CS Atrium - More than 40 ft | 2021_WA_BuildingCode | Atrium | Atrium - More than 40 ft | 255 | 255 | 0 | CS Atrium - More than 40 ft_2021WABuildingCode | CS Atrium - More than 40 ft_2021WABuildingCodeScheduleSet | [9 empty] | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_Corridors other than Group RVent | [6 empty] | 6.4584 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Atrium - Above 40 feet in heightLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2015DOE_PrototypeSpace Function_Atrium - H > 13mInfil | Always On |  | 0.36 | 0 | MediumRough | 0.1294 | 3.01 | 886 | 1270 | 0.9 | 0.7 | 0.7 | Mixed_Atrium_GT40ft_129mm | CalculatedEstimateHeavyGlulamBeamsOrSteelMembersMixed_Atrium_GT40ft_129mmInternalMassDef
CS Banking Activity Area | 2021_WA_BuildingCode | Bank | Banking Activity Area | 204 | 255 | 229 | CS Banking Activity Area_2021WABuildingCode | CS Banking Activity Area_2021WABuildingCodeScheduleSet | 0.43056 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_Museums/galleries COMNET-REV9PeopleDef | NECB-A-Occupancy | CS Banking Activity AreaActivity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_Museums/galleries Vent | 18.5149 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Banking Activity AreaElectricalEquipDef | NECB-A-Electric-Equipment | 6.566 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Banking activity areaLightingDef | NECB-A-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2016DOE_PrototypeSpace Function_Bank - banking and officesInfil | Always On |  | 0.69 |  | MediumRough | 0.0151 | 5.243 | 1547 | 811 | 0.9 | 0.7 | 0.7 | Mixed_Banking_ActivityArea_15mm | CalculatedEstimateTellerCountersAndSecurityTransactionWindowsMixed_Banking_ActivityArea_15mmInternalMassDef
CS Classroom/Lecture/Training - Penitentiary | 2021_WA_BuildingCode | Penitentiary | Classroom/Lecture/Training | 204 | 120 | 230 | CS Classroom/Lecture/Training - Penitentiary_2021WABuildingCode | CS Classroom/Lecture/Training - Penitentiary_2021WABuildingCodeScheduleSet | 0.69965 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Education_Lecture classroom COMNET-REV9PeopleDef | NECB-D-Occupancy | CS Classroom/Lecture/Training - PenitentiaryActivity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Education_Lecture classroom Vent | 6.3414 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Classroom/Lecture/Training - PenitentiaryElectricalEquipDef | NECB-D-Electric-Equipment | 9.58 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Classroom/lecture hall/training room - In a penitentiaryLightingDef | NECB-D-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Classroom/lecture/trainingInfil | Always On |  | 0.85 | 0 | MediumSmooth | 0.0043 | 9.44 | 1923 | 895 | 0.9 | 0.55 | 0.5 | Mixed_Classroom_Penitentiary_4mm | CalculatedEstimateLaminateDeskSteelChairInstitutionalMixed_Classroom_Penitentiary_4mmInternalMassDef
CS Classroom/Lecture/Training - K-12 - laboratory and shops | 2021_WA_BuildingCode | Secondary School | Classroom/Lecture/Training - K-12 - laboratory and shops | 204 | 120 | 230 | CS Classroom/Lecture/Training - K-12 - laboratory and shops_2021WABuildingCode | CS Classroom/Lecture/Training - K-12 - laboratory and shops_2021WABuildingCodeScheduleSet | 0.69965 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Education_Lecture classroom COMNET-REV9PeopleDef | SchoolSecondary BLDG_OCC_SCH_Gym | CS Classroom/Lecture/Training - K-12 - laboratory and shopsActivity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Education_Lecture classroom Vent | 6.3414 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Classroom/Lecture/Training - K-12 - laboratory and shopsElectricalEquipDef | SchoolSecondary BLDG_EQUIP_SCH | 11.948 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Laboratory - In or as a classroomsLightingDef | SchoolSecondary BLDG_LIGHT_GYM_SCH | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeSecondarySchool_ClassroomInfil | Always On |  | 2.35 | 0 | MediumRough | 0.00428 | 14 | 2572 | 659 | 0.9 | 0.7 | 0.7 | Mixed_ClassroomK12_LabShop_4mm | CalculatedEstimateSteelBenchesCaseworkAndShopMachinesMixed_ClassroomK12_LabShop_4mmInternalMassDef
CS Classroom/Lecture/Training - Other | 2021_WA_BuildingCode | School/University | Classroom/Lecture/Training | 204 | 120 | 230 | CS Classroom/Lecture/Training - Other_2021WABuildingCode | CS Classroom/Lecture/Training - Other_2021WABuildingCodeScheduleSet | 0.69965 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Education_Lecture classroom COMNET-REV9BA School/UniversityPeopleDef | NECB-D-Occupancy | CS Classroom/Lecture/Training - OtherActivity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Education_Lecture classroom Vent | 6.3414 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Classroom/Lecture/Training - OtherElectricalEquipDef | NECB-D-Electric-Equipment | 7.6424 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Classroom/lecture hall/training room - OtherwiseLightingDef | NECB-D-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Classroom/lecture/trainingInfil | Always On |  | 1.3 | 0 | MediumRough | 0.0078 | 2.85 | 894 | 936 | 0.9 | 0.6 | 0.6 | Mixed_ClassroomTraining_Other_8mm | CalculatedEstimateMovableLaminateTablesAndStackingChairsMixed_ClassroomTraining_Other_8mmInternalMassDef
CS Conference/Meeting/Multipurpose | 2021_WA_BuildingCode | Office | Conference/Meeting/Multipurpose | 230 | 196 | 120 | CS Conference/Meeting/Multipurpose_2021WABuildingCode | CS Conference/Meeting/Multipurpose_2021WABuildingCodeScheduleSet | 0.5382 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Office_Conference roomsCOMNET-REV9BA OfficePeopleDef | OfficeMedium BLDG_OCC_SCH | CS Conference/Meeting/MultipurposeActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Office_Conference roomsVent | 7.8926 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Conference/Meeting/MultipurposeElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 10.4411 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Conference/meeting/multipurposeLightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Conf./meet./multi-purposeInfil | Always On |  | 0.61 | 0 | MediumRough | 0.0059 | 42.8 | 1804 | 1243 | 0.9 | 0.7 | 0.65 | Conference_Meeting_Multipurpose_Material | CalculatedEstimateConferenceTablesChairsAndCredenzaConference_Meeting_Multipurpose_MaterialInternalMassDef
CS Confinment Cells | 2021_WA_BuildingCode | Courthouse | Confinment Cells | 192 | 192 | 192 | CS Confinment Cells_2021WABuildingCode | CS Confinment Cells_2021WABuildingCodeScheduleSet | 0.2691 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Correctional facilities_Cells With plumbing fixturesCOMNET-REV9BA OfficePeopleDef | NECB-H-Occupancy | CS Confinment CellsActivity | 0.0023596 | 0.0006096 |  | Washington State Mechanical Code TABLE 403.3.1.1Correctional facilities_Cells With plumbing fixturesVent | 16.0688 | 0 | 0.5 | 0 | COMNET-REV9NREL 956/Eley AnalysisDOEPrototypeCS Confinment CellsElectricalEquipDef | NECB-H-Electric-Equipment | 7.5348 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Confinement cellLightingDef | NECB-H-Lighting | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeOffice_ConferenceInfil | OfficeMedium INFIL_SCH_PNNL |  | 0.73 | 0 | Smooth | 0.0043 | 33.8 | 7746 | 492 | 0.9 | 0.7 | 0.7 | Steel_Security_Fixtures_4mm | CalculatedEstimateFixedSteelBedDeskAndToiletFixturesSteel_Security_Fixtures_4mmInternalMassDef
CS Copy/Print Room | 2021_WA_BuildingCode | Office | Copy/Print Room | 41 | 31 | 169 | CS Copy/Print Room_2021WABuildingCode | CS Copy/Print Room_2021WABuildingCodeScheduleSet | 0.043056 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Workrooms_Copy_printing rooms COMNET-REV9BA OfficePeopleDef | OfficeMedium BLDG_OCC_SCH | CS Copy/Print RoomActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Workrooms_Copy_printing rooms Vent | 17.9987 | 0 | 0.5 | 0 | COMNET-REV9BA OfficeWholeBuildingCS Copy/Print RoomElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 3.3368 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Copy/print roomLightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeOffice_PrintRoomInfil | OfficeMedium INFIL_SCH_PNNL |  | 1.52 | 0 | MediumRough | 0.0015 | 39.6 | 6545 | 629 | 0.9 | 0.7 | 0.65 | Steel_Office_Equipment_2mm | CalculatedEstimateCommercialCopierAndSteelStorageCabinetsSteel_Office_Equipment_2mmInternalMassDef
CS Corridor - Assisted Living | 2021_WA_BuildingCode | Assisted Living | Corridor | 169 | 31 | 31 | CS Corridor - Assisted Living_2021WABuildingCode | CS Corridor - Assisted Living_2021WABuildingCodeScheduleSet | [9 empty] | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_Corridors serving Group R Vent | 15.1196 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Corridor - Assisted LivingElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 7.6424 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Corridor - In a facility for the visually impaired (and not used primarily by the staff)LightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeMidriseApartment_CorridorInfil | ApartmentMidRise INF_APT_SCH |  | 0.19 | 0 | Smooth | 0.0027 | 182.5 | 3009 | 894 | 0.9 | 0.7 | 0.7 | Aluminum_Corridor_Fixtures_3mm | CalculatedEstimateAluminumHandrailsAndWayfindingSignageAluminum_Corridor_Fixtures_3mmInternalMassDef
CS Corridor - Hospital | 2021_WA_BuildingCode | Hospital | Corridor | 169 | 31 | 31 | CS Corridor - Hospital_2021WABuildingCode | CS Corridor - Hospital_2021WABuildingCodeScheduleSet | [9 empty] | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_Corridors other than Group RVent | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Corridor - HospitalElectricalEquipDef | Hospital BLDG_EQUIP_SCH | 7.6424 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Corridor - In a hospitalLightingDef | Hospital BLDG_LIGHT_CORRIDOR_SCH | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeHospital_CorridorInfil | Hospital INFIL_SCH_PNNL |  | 0.26 | 0 | Smooth | 0.0025 | 64.8 | 6330 | 644 | 0.9 | 0.7 | 0.7 | Stainless_Aluminum_Hospital_3mm | CalculatedEstimateStainlessHandrailsAndMedicalSignageStainless_Aluminum_Hospital_3mmInternalMassDef
CS Corridor - Manufacturing | 2021_WA_BuildingCode | Manufacturing Facility | Corridor | 169 | 31 | 31 | CS Corridor - Manufacturing_2021WABuildingCode | CS Corridor - Manufacturing_2021WABuildingCodeScheduleSet | 0.075272 | 424.9707 | 97 | 120 | 0.4 | COMNET-REV9CS Corridor - ManufacturingPeopleDef | NECB-A-Occupancy | CS Corridor - ManufacturingActivity |  | 0.00127 |  | COMNET-REV9CS Corridor - ManufacturingVent | 3.7116 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Corridor - ManufacturingElectricalEquipDef | NECB-A-Electric-Equipment | 4.4132 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Corridor - In a manufacturing facilityLightingDef | NECB-A-Lighting | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeOffice_CorridorInfil | OfficeMedium INFIL_SCH_PNNL |  | 0.34 | 0 | MediumRough | 0.0063 | 82 | 5095 | 711 | 0.9 | 0.7 | 0.7 | Steel_Aluminum_Industrial_6mm | CalculatedEstimateSteelHandrailsAndSafetyBollardsSteel_Aluminum_Industrial_6mmInternalMassDef
CS Corridor - Other | 2021_WA_BuildingCode | Miscellaneous | Corridor | 169 | 31 | 31 | CS Corridor - Other_2021WABuildingCode | CS Corridor - Other_2021WABuildingCodeScheduleSet | [9 empty] | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_Corridors other than Group RVent | 3.2292 | 0 | 0.5 | 0 | COMNET-REV9BA WarehouseWholeBuildingCS Corridor - OtherElectricalEquipDef | SchoolSecondary BLDG_EQUIP_SCH | 4.4132 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Corridor - OtherwiseLightingDef | SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | [6 empty] | 9.081e-06 | PNNL-90.1-2013DOE_PrototypeLargeHotel_CorridorInfil | HotelLarge INFIL_QUARTER_ON_SCH |  | 0.19 | 0 | Smooth | 0.0027 | 186.9 | 2928 | 898 | 0.9 | 0.7 | 0.7 | Aluminum_Commercial_Fixtures_3mm | CalculatedEstimateAluminumHandrailsAndDirectionalSignageAluminum_Commercial_Fixtures_3mmInternalMassDef
CS Courtroom | 2021_WA_BuildingCode | Courthouse | Courtroom | 153 | 76 | 0 | CS Courtroom_2021WABuildingCode | CS Courtroom_2021WABuildingCodeScheduleSet | 0.75347 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_CourtroomsCOMNET-REV9PeopleDef | NECB-A-Occupancy | CS CourtroomActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces_CourtroomsVent | 16.0688 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS CourtroomElectricalEquipDef | NECB-A-Electric-Equipment | 12.9168 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2CourtroomLightingDef | NECB-A-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Courthouse - courtroomInfil | Always On |  | 0.84 |  | MediumRough | 0.024 | 3.54 | 596 | 1580 | 0.9 | 0.7 | 0.65 | Wood_Courtroom_Furniture_24mm | CalculatedEstimateSolidHardwoodBenchesAndGallerySeatingWood_Courtroom_Furniture_24mmInternalMassDef
CS Computer Room | 2021_WA_BuildingCode | Office | Computer Room | 41 | 31 | 169 | CS Computer Room_2021WABuildingCode | CS Computer Room_2021WABuildingCodeScheduleSet | 0.043056 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Workrooms_Computer without printingCOMNET-REV9BA OfficePeopleDef | OfficeMedium BLDG_OCC_SCH | CS Computer RoomActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Workrooms_Computer without printingVent | 645.84 | 0 | 0.5 | 0 | EstimateDOEPrototypeCS Computer RoomElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 10.1182 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Computer room, data centerLightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeOffice_IT_RoomInfil | OfficeMedium INFIL_SCH_PNNL |  | 1.62 |  | MediumRough | 0.0022 | 59 | 4439 | 844 | 0.9 | 0.7 | 0.65 | Steel_IT_Equipment_2mm | CalculatedEstimateITWorkstationsAndServerRackSteel_IT_Equipment_2mmInternalMassDef
CS Dining Area - Penitentiary | 2021_WA_BuildingCode | Penitentiary | Dining Area | 31 | 169 | 34 | CS Dining Area - Penitentiary_2021WABuildingCode | CS Dining Area - Penitentiary_2021WABuildingCodeScheduleSet | 0.75347 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Dining roomsCOMNET-REV9PeopleDef | NECB-B-Occupancy | CS Dining Area - PenitentiaryActivity | 0.0035394 | 0.0009144 |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Dining roomsVent | 13.5949 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Dining Area - PenitentiaryElectricalEquipDef | NECB-B-Electric-Equipment | 4.5209 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Dining area - In a penitentiaryLightingDef | NECB-B-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Penitentiary - diningInfil | Always On |  | 0.74 |  | Smooth | 0.0027 | 42.6 | 7746 | 478 | 0.9 | 0.7 | 0.7 | Steel_Security_Dining_3mm | CalculatedEstimateFixedSteelTableBenchUnitsSteel_Security_Dining_3mmInternalMassDef
CS Dining Area - Assisted Living | 2021_WA_BuildingCode | Hotel/Motel | Dining Area | 31 | 169 | 34 | CS Dining Area - Assisted Living_2021WABuildingCode | CS Dining Area - Assisted Living_2021WABuildingCodeScheduleSet | 0.75347 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Dining roomsCOMNET-REV9PeopleDef | NECB-B-Occupancy | CS Dining Area - Assisted LivingActivity | 0.0035394 | 0.0009144 |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Dining roomsVent | 14.166 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Dining Area - Assisted LivingElectricalEquipDef | NECB-B-Electric-Equipment | 13.6703 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Dining area - In a facility for the visually impaired (and not used primarily by the staff)LightingDef | NECB-B-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeDining - family_WholeBuildingInfil | Always On |  | 1.44 |  | MediumRough | 0.0074 | 6.95 | 877 | 1320 | 0.9 | 0.7 | 0.65 | Wood_Composite_Residential_7mm | CalculatedEstimateResidentialStyleDiningFurnitureWood_Composite_Residential_7mmInternalMassDef
CS Dining Area - Bar Lounge/Leisure | 2021_WA_BuildingCode | Bar/Lounge | Dining Area | 31 | 169 | 34 | CS Dining Area - Bar Lounge/Leisure _2021WABuildingCode | CS Dining Area - Bar Lounge/Leisure _2021WABuildingCodeScheduleSet | 1.0764 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Bars_cocktail loungesCOMNET-REV9PeopleDef | NECB-B-Occupancy | CS Dining Area - Bar Lounge/Leisure Activity | 0.0035394 | 0.0009144 |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Bars_cocktail loungesVent | 13.5949 | 0.25 | 0.3 | 0 | COMNET-REV9DOEPrototypeCS Dining Area - Bar Lounge/Leisure ElectricalEquipDef | NECB-B-Electric-Equipment | 9.257 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Dining area - In a bar/lounge or leisure diningLightingDef | NECB-B-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Dining - bar lounge/leisureInfil | Always On |  | 1.79 |  | MediumRough | 0.0028 | 9.72 | 2241 | 1189 | 0.9 | 0.7 | 0.65 | Mixed_Commercial_BarLounge_3mm | CalculatedEstimateBarCounterAndMixedSeatingMixed_Commercial_BarLounge_3mmInternalMassDef
CS Dining Area - Cafeteria or Fast Food | 2021_WA_BuildingCode | Quick Service Restaurant | Dining Area | 31 | 169 | 34 | CS Dining Area - Cafeteria or Fast Food _2021WABuildingCode | CS Dining Area - Cafeteria or Fast Food _2021WABuildingCodeScheduleSet | 1.0764 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Cafeteria_fast food COMNET-REV9PeopleDef | RestaurantFastFood BLDG_OCC_SCH | CS Dining Area - Cafeteria or Fast Food Activity | 0.0035394 | 0.0009144 |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Cafeteria_fast food Vent | 14.729 | 0.25 | 0.3 | 0 | COMNET-REV9DOEPrototypeCS Dining Area - Cafeteria or Fast Food ElectricalEquipDef | RestaurantFastFood BLDG_EQUIP_SCH | 4.3056 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Dining area - In cafeteria or fast food diningLightingDef | RestaurantFastFood BLDG_LIGHT_DINING_SCH_2013 | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeDining - cafeteria_WholeBuildingInfil | Always On |  | 1.68 |  | Smooth | 0.0027 | 19.2 | 2705 | 1099 | 0.9 | 0.7 | 0.65 | Laminate_Commercial_FastFood_3mm | CalculatedEstimateFixedBoothAndMoldedChairsLaminate_Commercial_FastFood_3mmInternalMassDef
CS Dining Area - Family Dining | 2021_WA_BuildingCode | Restaurant | Dining Area | 31 | 169 | 34 | CS Dining Area - Family Dining _2021WABuildingCode | CS Dining Area - Family Dining _2021WABuildingCodeScheduleSet | 0.75347 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Dining roomsCOMNET-REV9PeopleDef | NECB-B-Occupancy | CS Dining Area - Family Dining Activity | 0.0035394 | 0.0009144 |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Dining roomsVent | 14.166 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Dining Area - Family Dining ElectricalEquipDef | NECB-B-Electric-Equipment | 6.4584 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Dining area - In a family dining areaLightingDef | NECB-B-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeDining - family_WholeBuildingInfil | Always On |  | 2.9 |  | MediumRough | 0.0055 | 4.74 | 802 | 1360 | 0.9 | 0.7 | 0.65 | Wood_Composite_Family_Dining_6mm | CalculatedEstimateBoothSeatingAndUpholsteredChairsWood_Composite_Family_Dining_6mmInternalMassDef
CS Dining Area - Other | 2021_WA_BuildingCode | Dining - other | Dining Area | 31 | 169 | 34 | CS Dining Area - Other_2021WABuildingCode | CS Dining Area - Other_2021WABuildingCodeScheduleSet | 0.75347 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Dining roomsCOMNET-REV9PeopleDef | NECB-B-Occupancy | CS Dining Area - OtherActivity | 0.0035394 | 0.0009144 |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Dining roomsVent | 14.166 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Dining Area - OtherElectricalEquipDef | NECB-B-Electric-Equipment | 4.6285 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Dining area - OtherwiseLightingDef | NECB-B-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Dining - otherInfil | Always On |  | 2.43 |  | MediumRough | 0.0028 | 5.29 | 1440 | 1288 | 0.9 | 0.7 | 0.65 | Mixed_Commercial_Dining_3mm | CalculatedEstimateGenericBoothAndTableSeatingMixed_Commercial_Dining_3mmInternalMassDef
CS Electrical/Mechanical | 2021_WA_BuildingCode | Elec/Mech Room | Electrical/Mechanical | 41 | 31 | 175 | CS Electrical/Mechanical_2021WABuildingCode | CS Electrical/Mechanical_2021WABuildingCodeScheduleSet | [9 empty] | 0.0006096 |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Storage roomsVent | 17.9987 | 0 | 0.5 | 0 | COMNET-REV9BA OfficeWholeBuildingCS Electrical/MechanicalElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 4.6285 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Electrical/mechanicalLightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Electrical/MechanicalInfil | Always On |  | 3.48 |  | Smooth | 0.0028 | 56.7 | 7047 | 511 | 0.9 | 0.7 | 0.7 | Steel_Mechanical_Equipment_3mm | CalculatedEstimateHVACAndElectricalEquipmentSteel_Mechanical_Equipment_3mmInternalMassDef
CS Emergency Vehicle Garage | 2021_WA_BuildingCode | Parking Garage | Emergency Vehicle Garage | 153 | 0 | 76 | CS Emergency Vehicle Garage_2021WABuildingCode | CS Emergency Vehicle Garage_2021WABuildingCodeScheduleSet | [11 empty] | Washington State Mechanical Code TABLE 403.3.1.1Storage_Repair garages_enclosed parking garageVent | 6.2009 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Emergency Vehicle GarageElectricalEquipDef | NECB-H-Electric-Equipment | 5.5973 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Emergency vehicle garageLightingDef | NECB-H-Lighting | [6 empty] | 9.4389e-05 | EstimateSpace Function_Parking garage spaceInfil | Always On |  | 1.1 |  | MediumRough | 0.0017 | 45.8 | 7368 | 517 | 0.9 | 0.7 | 0.7 | Steel_Emergency_Garage_2mm | CalculatedEstimateApparatusBayStorageAndLockersSteel_Emergency_Garage_2mmInternalMassDef
CS Food Preparation - Gas Cooking | 2021_WA_BuildingCode | Commercial Kitchen | Food Preparation - Gas Cooking | 255 | 178 | 102 | CS Food Preparation - Gas Cooking_2021WABuildingCode | CS Food Preparation - Gas Cooking_2021WABuildingCodeScheduleSet | 0.21528 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Kitchens (cooking)ASHRAEHB2025FundCh18tbl4Sendentary work_RestaurantPeopleDef | NECB-B-Occupancy | CS Food Preparation - Gas CookingActivity | 0.0035394 | 0.0006096 |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Kitchens (cooking)Vent | 14.166 | 0.25 | 0.3 | 0.2 | COMNET-REV9DOEPrototypeCS Food Preparation - Gas CookingElectricalEquipDef | NECB-B-Electric-Equipment | 11.7328 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Food preparationLightingDef | NECB-B-Lighting | 377.4935 | 0.1 | 0.2 | 0.7 | COMNET-REV9California Commercial End-Use Survey (CEUS)DOEPrototypeCS Food Preparation - Gas CookingGasEquipDef | RestaurantFastFood FF_GAS_EQUIP_SCH | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Food preparationInfil | Always On |  | 2.2 |  | Smooth | 0.0023 | 22.8 | 7656 | 515 | 0.9 | 0.7 | 0.7 | Stainless_Commercial_Kitchen_2mm | CalculatedEstimateGasCookingEquipmentAndStainlessPrepStainless_Commercial_Kitchen_2mmInternalMassDef
CS Guest Room | 2021_WA_BuildingCode | Hotel/Motel | Guest Room | 78 | 167 | 222 | CS Guest Room_2021WABuildingCode | CS Guest Room_2021WABuildingCodeScheduleSet | 0.10764 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Hotels,_motels_resorts_dormitories_Bedroom/living room COMNET-REV9PeopleDef | HotelLarge GuestRoom_Occ_Sch | CS Guest RoomActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels,_motels_resorts_dormitories_Bedroom/living room Vent | 16.8363 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Guest RoomElectricalEquipDef | HotelLarge GuestRoom_Eqp_Sch_Adva | 4.4132 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Guest roomLightingDef | HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | [6 empty] | 5.2858e-05 | PNNL-90.1-2013DOE_PrototypeLargeHotel_GuestRoomInfil | HotelLarge INFIL_QUARTER_ON_SCH |  | 1.79 |  | MediumRough | 0.0097 | 3.27 | 1155 | 1293 | 0.9 | 0.7 | 0.65 | Mixed_Hotel_Furniture_10mm | CalculatedEstimateBedDresserAndCaseGoodsMixed_Hotel_Furniture_10mmInternalMassDef
CS Judges Chambers | 2021_WA_BuildingCode | Courthouse | Judges Chambers | 153 | 153 | 0 | CS Judges Chambers_2021WABuildingCode | CS Judges Chambers_2021WABuildingCodeScheduleSet | 0.05382 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Office_Office spacesCOMNET-REV9PeopleDef | NECB-A-Occupancy | CS Judges ChambersActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Office_Office spacesVent | 16.0688 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Judges ChambersElectricalEquipDef | NECB-A-Electric-Equipment | 7.9654 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Office - Enclosed <= 250LightingDef | NECB-A-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Courthouse - chambersInfil | Always On |  | 4.06 |  | MediumRough | 0.0062 | 4.93 | 1520 | 1343 | 0.9 | 0.7 | 0.65 | Wood_Legal_Library_6mm | CalculatedEstimateLawBookShelvingAndExecutiveFurnitureWood_Legal_Library_6mmInternalMassDef
CS Laboratory - Classrooms | 2021_WA_BuildingCode | School/University | Laboratory - Classrooms | 224 | 224 | 224 | CS Laboratory - Classrooms _2021WABuildingCode | CS Laboratory - Classrooms _2021WABuildingCodeScheduleSet | 0.2691 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Education - Science laboratoriesCOMNET-REV9BA School/UniversityPeopleDef | NECB-D-Occupancy | CS Laboratory - Classrooms Activity | 0.0047192 | 0.0009144 |  | Washington State Mechanical Code TABLE 403.3.1.1Education - Science laboratoriesVent | 35.9683 | 0.2 | 0.5 | 0.1 | COMNET-REV9EstimateCS Laboratory - Classrooms ElectricalEquipDef | NECB-D-Electric-Equipment | 11.948 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Laboratory - In or as a classroomsLightingDef | NECB-D-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Lab - classroomsInfil | Always On |  | 3.6 |  | Smooth | 0.0017 | 32.4 | 4900 | 833 | 0.9 | 0.7 | 0.7 | Steel_Lab_Equipment_2mm | CalculatedEstimateLabBenchesFumeHoodAndStorageSteel_Lab_Equipment_2mmInternalMassDef
CS Laboratory - Other | 2021_WA_BuildingCode | Laboratory | Laboratory - Other | 224 | 224 | 224 | CS Laboratory - Other_2021WABuildingCode | CS Laboratory - Other_2021WABuildingCodeScheduleSet | 0.2691 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Education - Science laboratoriesCOMNET-REV9BA School/UniversityPeopleDef | NECB-A-Occupancy | CS Laboratory - OtherActivity | 0.0047192 | 0.0009144 |  | Washington State Mechanical Code TABLE 403.3.1.1Education - Science laboratoriesVent | 35.9683 | 0.2 | 0.5 | 0.1 | COMNET-REV9EstimateCS Laboratory - OtherElectricalEquipDef | NECB-A-Electric-Equipment | 14.3161 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Laboratory - OtherwiseLightingDef | NECB-A-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Lab - researchInfil | Always On |  | 4.53 |  | Smooth | 0.0023 | 34.2 | 6792 | 592 | 0.9 | 0.7 | 0.7 | Steel_Research_Lab_2mm | CalculatedEstimateResearchBenchesFumeHoodsAndStorageSteel_Research_Lab_2mmInternalMassDef
CS Laundry/Washing Area | 2021_WA_BuildingCode | Commercial Laundry | Laundry/Washing Area | 120 | 149 | 230 | CS Laundry/Washing Area_2021WABuildingCode | CS Laundry/Washing Area_2021WABuildingCodeScheduleSet | 0.10764 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1Dry cleaners, laundries - Commercial laundryASHRAEHB2025FundCh18tbl4Sendentary work_RestaurantPeopleDef | HotelSmall LaundryRoom_Occ_Sch | CS Laundry/Washing AreaActivity | 0.0023596 | 0.0006096 |  | Washington State Mechanical Code TABLE 403.3.1.1Dry cleaners, laundries - Commercial laundryVent | 5.5878 | 0.2 | 0.2 | 0.4 | COMNET-REV9EstimateCS Laundry/Washing AreaElectricalEquipDef | HotelSmall LaundryRoom_Eqp_Elec_Sch | 5.7049 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Laundry/washing areaLightingDef | HotelSmall BLDG_LIGHT_LAUNDRY_SCH | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Hospital - laundry/washingInfil | Always On |  | 1.92 |  | Smooth | 0.0023 | 27.1 | 6662 | 565 | 0.9 | 0.7 | 0.7 | Steel_Laundry_Equipment_2mm | CalculatedEstimateCommercialWashersAndDryersSteel_Laundry_Equipment_2mmInternalMassDef
CS Loading Dock - Interior | 2021_WA_BuildingCode | Warehouse | Loading Dock - Interior | 153 | 153 | 255 | CS Loading Dock - Interior_2021WABuildingCode | CS Loading Dock - Interior_2021WABuildingCodeScheduleSet | 0.021528 | 219.8124 | 97 | 120 | 0.36667 | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Shipping and receivingCOMNET-REV9PeopleDef | NECB-A-Occupancy | CS Loading Dock - InteriorActivity | 0.0047192 | 0.0006096 |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Shipping and receivingVent | 1.0764 | 0 | 0.5 | 0 | DOEPrototypeCS Loading Dock - InteriorElectricalEquipDef | NECB-A-Electric-Equipment | 9.4723 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Loading dock, interiorLightingDef | NECB-A-Lighting | [6 empty] | 9.4389e-05 | EstimateSpace Function_Warehouse - med/blkInfil | Always On |  | 1.07 |  | MediumRough | 0.0036 | 75.6 | 6355 | 589 | 0.9 | 0.7 | 0.7 | Steel_Warehouse_Equipment_4mm | CalculatedEstimatePalletRackingAndDockEquipmentSteel_Warehouse_Equipment_4mmInternalMassDef
CS Lobby - Assisted Living | 2021_WA_BuildingCode | Hotel/Motel | Lobby | 230 | 157 | 120 | CS Lobby - Assisted Living_2021WABuildingCode | CS Lobby - Assisted Living_2021WABuildingCodeScheduleSet | 0.32292 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Lobbies/prefunctionCOMNET-REV9PeopleDef | NECB-H-Occupancy | CS Lobby - Assisted LivingActivity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Lobbies/prefunctionVent | 15.1196 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Lobby - Assisted LivingElectricalEquipDef | NECB-H-Electric-Equipment | 18.1912 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Lobby - In a facility for the visually impaired (and not used primarily by the staff)LightingDef | NECB-H-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Hotel/Motel - lobbyInfil | Always On |  | 2.13 |  | MediumRough | 0.0045 | 4.19 | 1362 | 1313 | 0.9 | 0.7 | 0.65 | Wood_Residential_Lobby_5mm | CalculatedEstimateResidentialLoungeFurnitureWithPianoWood_Residential_Lobby_5mmInternalMassDef
CS Lobby - Elevator | 2021_WA_BuildingCode | Miscellaneous | Lobby - Elevator | 230 | 157 | 120 | CS Lobby - Elevator _2021WABuildingCode | CS Lobby - Elevator _2021WABuildingCodeScheduleSet | [9 empty] | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Corridors serving other than Group R occupanciesVent | 3.2292 | 0 | 0.5 | 0 | COMNET-REV9BA WarehouseWholeBuildingCS Lobby - Elevator ElectricalEquipDef | NECB-C-Electric-Equipment | 6.9966 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Lobby - For an elevatorLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Lobby - elevatorInfil | Always On |  | 0.55 |  | Smooth | 0.0022 | 65.6 | 3739 | 961 | 0.9 | 0.7 | 0.7 | Metal_Elevator_Lobby_2mm | CalculatedEstimateMinimalBenchAndDirectoryBoardMetal_Elevator_Lobby_2mmInternalMassDef
CS Lobby - Hotel | 2021_WA_BuildingCode | Hotel/Motel | Lobby | 230 | 157 | 120 | CS Lobby - Hotel_2021WABuildingCode | CS Lobby - Hotel_2021WABuildingCodeScheduleSet | 0.32292 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Lobbies/prefunctionCOMNET-REV9PeopleDef | HotelLarge BLDG_OCC_SCH | CS Lobby - HotelActivity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Lobbies/prefunctionVent | 16.8363 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Lobby - HotelElectricalEquipDef | HotelLarge BLDG_EQUIP_SCH | 5.4896 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Lobby - In a hotelLightingDef | HotelLarge BLDG_LIGHT_SCH | [6 empty] | 5.2858e-05 | PNNL-NECB 2011DOE_PrototypeLargeHotel_LobbyInfil | Always On |  | 1.88 |  | MediumRough | 0.0045 | 4.21 | 1601 | 1121 | 0.9 | 0.7 | 0.65 | Mixed_Hotel_Lobby_5mm | CalculatedEstimateFrontDeskSofasAndAreaRugsMixed_Hotel_Lobby_5mmInternalMassDef
CS Lobby - Motion Picture Theater | 2021_WA_BuildingCode | Theater | Lobby | 230 | 157 | 120 | CS Lobby - Motion Picture Theater _2021WABuildingCode | CS Lobby - Motion Picture Theater _2021WABuildingCodeScheduleSet | 1.6146 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1Theaters - LobbiesCOMNET-REV9PeopleDef | NECB-C-Occupancy | CS Lobby - Motion Picture Theater Activity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Theaters - LobbiesVent | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Lobby - Motion Picture Theater ElectricalEquipDef | NECB-C-Electric-Equipment | 2.4757 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Lobby - In a motion picture theaterLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Lobby - motion pictureInfil | Always On |  | 1.32 |  | Smooth | 0.0011 | 42.4 | 5971 | 655 | 0.9 | 0.7 | 0.7 | Steel_Theater_Equipment_1mm | CalculatedEstimateConcessionStandAndTicketKiosksSteel_Theater_Equipment_1mmInternalMassDef
CS Lobby - Performing Arts Theater | 2021_WA_BuildingCode | Theater | Lobby | 230 | 157 | 120 | CS Lobby - Performing Arts Theater _2021WABuildingCode | CS Lobby - Performing Arts Theater _2021WABuildingCodeScheduleSet | 1.6146 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1Theaters - LobbiesCOMNET-REV9PeopleDef | NECB-C-Occupancy | CS Lobby - Performing Arts Theater Activity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Theaters - LobbiesVent | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Lobby - Performing Arts Theater ElectricalEquipDef | NECB-C-Electric-Equipment | 13.455 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Lobby - In a performing arts theaterLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Lobby - performance artsInfil | Always On |  | 3.01 |  | MediumRough | 0.0043 | 3.32 | 1416 | 1196 | 0.9 | 0.7 | 0.65 | Mixed_Theater_Lobby_4mm | CalculatedEstimateCarpetedLobbyWithBarAndSeatingMixed_Theater_Lobby_4mmInternalMassDef
CS Lobby - Other | 2021_WA_BuildingCode | Miscellaneous | Lobby | 230 | 157 | 120 | CS Lobby - Other_2021WABuildingCode | CS Lobby - Other_2021WABuildingCodeScheduleSet | [9 empty] | 0.00508 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Elevator lobbies in parking garageVent | [6 empty] | 9.0418 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Lobby - OtherwiseLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Lobby - otherInfil | Always On |  | 0.71 |  | MediumRough | 0.0029 | 24.6 | 1775 | 1112 | 0.9 | 0.7 | 0.7 | Mixed_Commercial_Lobby_3mm | CalculatedEstimateBasicReceptionAndWaitingAreaMixed_Commercial_Lobby_3mmInternalMassDef
CS Locker Room | 2021_WA_BuildingCode | Miscellaneous | Locker Room | 0 | 153 | 153 | CS Locker Room_2021WABuildingCode | CS Locker Room_2021WABuildingCodeScheduleSet | [11 empty] | Washington State Mechanical Code TABLE 403.3.1.1Education - Locker/dressing roomsVent | 1.0764 | 0.2 | 0.5 | 0.1 | EstimateCS Locker RoomElectricalEquipDef | SchoolSecondary BLDG_EQUIP_SCH | 5.5973 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Locker roomLightingDef | SchoolSecondary BLDG_LIGHT_GYM_SCH | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Locker roomInfil | Always On |  | 3.66 |  | Smooth | 0.0011 | 42.3 | 7003 | 567 | 0.9 | 0.7 | 0.7 | Steel_LockerRoom_1mm | CalculatedEstimateMetalLockersAndBenchesSteel_LockerRoom_1mmInternalMassDef
CS Lounge/Break - Healthcare | 2021_WA_BuildingCode | Healthcare | Lounge/Break | 230 | 157 | 120 | CS Lounge/Break - Healthcare_2021WABuildingCode | CS Lounge/Break - Healthcare_2021WABuildingCodeScheduleSet | 0.2691 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Office - KitchenettesCOMNET-REV9BA Healthcare ClinicPeopleDef | OutPatientHealthCare BLDG_OCC_SCH | CS Lounge/Break - HealthcareActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Office - KitchenettesVent | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Lounge/Break - HealthcareElectricalEquipDef | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | 4.5209 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Lounge /breakroom - In a health care facilityLightingDef | OutPatientHealthCare BLDG_LIGHT_SCH | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeOutpatient_LoungeInfil | OutPatientHealthCare INFIL_SCH |  | 2.29 |  | MediumRough | 0.0022 | 15.9 | 2558 | 1034 | 0.9 | 0.7 | 0.7 | Mixed_Healthcare_Lounge_2mm | CalculatedEstimateKitchenetteAndDiningFurnitureMixed_Healthcare_Lounge_2mmInternalMassDef
CS Lounge/Break - Other | 2021_WA_BuildingCode | Miscellaneous | Lounge/Break | 230 | 157 | 120 | CS Lounge/Break - Other_2021WABuildingCode | CS Lounge/Break - Other_2021WABuildingCodeScheduleSet | 0.2691 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Office - KitchenettesCOMNET-REV9BA OfficePeopleDef | OfficeMedium BLDG_OCC_SCH | CS Lounge/Break - OtherActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Office - KitchenettesVent | 17.9987 | 0.25 | 0.3 | 0 | COMNET-REV9BA OfficeWholeBuildingCS Lounge/Break - OtherElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 6.3508 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Lounge /breakroom - OtherwiseLightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeOffice_BreakRoomInfil | OfficeMedium INFIL_SCH_PNNL |  | 2.83 |  | Smooth | 0.0019 | 23.7 | 4488 | 869 | 0.9 | 0.7 | 0.7 | Steel_Break_Room_2mm | CalculatedEstimateVendingMachinesAndKitchenetteSteel_Break_Room_2mmInternalMassDef
CS Office - Enclosed | 2021_WA_BuildingCode | Office | Office - Enclosed | 120 | 230 | 199 | CS Office - Enclosed_2021WABuildingCode | CS Office - Enclosed_2021WABuildingCodeScheduleSet | 0.05382 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Office - Office spacesCOMNET-REV9PeopleDef | OfficeMedium BLDG_OCC_SCH | CS Office - EnclosedActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Office - Office spacesVent | 17.9987 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Office - EnclosedElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 7.9654 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Office - Enclosed <= 250LightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeOffice_ClosedOfficeInfil | OfficeMedium INFIL_SCH_PNNL |  | 2.99 |  | Smooth | 0.0014 | 23.9 | 4513 | 864 | 0.9 | 0.7 | 0.7 | Steel_Office_Furniture_1mm | CalculatedEstimateDeskFilingCabinetsAndBookshelfSteel_Office_Furniture_1mmInternalMassDef
CS Office - Open Plan | 2021_WA_BuildingCode | Office | Office - Open Plan | 120 | 230 | 199 | CS Office - Open Plan_2021WABuildingCode | CS Office - Open Plan_2021WABuildingCodeScheduleSet | 0.64583 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019Office Buildings - Telephone/data entryCOMNET-REV9PeopleDef | OfficeMedium BLDG_OCC_SCH | CS Office - Open PlanActivity | 0.0023596 | 0.0003048 |  | ASHRAE 62.1-2019Office Buildings - Telephone/data entryVent | 17.9987 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Office - Open PlanElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 6.566 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Office - Open planLightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeOffice_OpenOfficeInfil | OfficeMedium INFIL_SCH_PNNL |  | 3.22 |  | MediumRough | 0.0055 | 8.98 | 2130 | 1138 | 0.9 | 0.7 | 0.7 | Particleboard_Office_Panels_5mm | CalculatedEstimateCubiclePanelsAndWorkstationsParticleboard_Office_Panels_5mmInternalMassDef
CS Parking Area - Interior | 2021_WA_BuildingCode | Parking Garage | Parking Area - Interior | 153 | 0 | 76 | CS Parking Area - Interior_2021WABuildingCode | CS Parking Area - Interior_2021WABuildingCodeScheduleSet | [11 empty] | Washington State Mechanical Code TABLE 403.3.1.1Storage_Repair garages_enclosed parking garageVent | 3.2292 | 0 | 0.06 | 0.88 | Medium Estimate: Workplace, 20% of Spaces with Level 2 Charger12%lost to heatCS Parking Area - InteriorElectricalEquipDef | NECB-H-Electric-Equipment | 1.6146 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Parking area, interiorLightingDef | NECB-H-Lighting | [6 empty] | 9.4389e-05 | EstimateSpace Function_Parking garage spaceInfil | Always On |  | 2.68 |  | Smooth | 0.006 | 31.1 | 5865 | 669 | 0.9 | 0.7 | 0.65 | Steel_Vehicles_6mm | CalculatedEstimateParkedVehiclesAt60PercentOccupancySteel_Vehicles_6mmInternalMassDef
CS Pharmacy Area | 2021_WA_BuildingCode | Healthcare | Pharmacy Area | 255 | 0 | 127 | CS Pharmacy Area_2021WABuildingCode | CS Pharmacy Area_2021WABuildingCodeScheduleSet | 0.10764 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Workrooms - Pharmacy (prep area)COMNET-REV9PeopleDef | NECB-C-Occupancy | CS Pharmacy AreaActivity | 0.0023596 | 0.0009144 |  | Washington State Mechanical Code TABLE 403.3.1.1Workrooms - Pharmacy (prep area)Vent | 5.9124 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Pharmacy AreaElectricalEquipDef | NECB-C-Electric-Equipment | 17.8682 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Pharmacy areaLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Hospital - pharmacyInfil | Always On |  | 4.02 |  | MediumRough | 0.0026 | 14.3 | 3052 | 1139 | 0.9 | 0.7 | 0.7 | Mixed_Pharmacy_3mm | CalculatedEstimateMedicationShelvingAndStorageCabinetsMixed_Pharmacy_3mmInternalMassDef
CS Restrooms - Assisted Living | 2021_WA_BuildingCode | Assisted Living | Restrooms | 169 | 169 | 31 | CS Restrooms - Assisted Living_2021WABuildingCode | CS Restrooms - Assisted Living_2021WABuildingCodeScheduleSet | [10 empty] | 7 | Rule of ThumbHotels, motels, resorts and dormitories - Bathrooms/toilets - privateWashington State Mechanical Code TABLE 403.3.1.6 - 25/50 per fixtureVent | 15.1196 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Restrooms - Assisted LivingElectricalEquipDef | OfficeMedium BLDG_EQUIP_SCH | 13.5626 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Restroom - In a facility for the visually impaired (and not used primarily by the staff)LightingDef | OfficeMedium BLDG_LIGHT_SCH_2013 | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeOffice_RestroomInfil | OfficeMedium INFIL_SCH_PNNL |  | 3.22 |  | Smooth | 0.0045 | 7.51 | 2167 | 1148 | 0.9 | 0.7 | 0.7 | Phenolic_Restroom_4mm | CalculatedEstimateADAFixturesWithGrabBarsAndShowerPhenolic_Restroom_4mmInternalMassDef
CS Restrooms - Other | 2021_WA_BuildingCode | Miscellaneous | Restrooms | 169 | 169 | 31 | CS Restrooms - Other_2021WABuildingCode | CS Restrooms - Other_2021WABuildingCodeScheduleSet | [10 empty] | 12 | Rule of ThumbPublic spaces - Toilet rooms - PublicWashington State Mechanical Code TABLE 403.3.1.6 - 50/70 per fixtureVent | 3.2292 | 0 | 0.5 | 0 | COMNET-REV9BA WarehouseWholeBuildingCS Restrooms - OtherElectricalEquipDef | HotelSmall Lobby_Eqp_Sch | 6.7813 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Restroom - OtherwiseLightingDef | HotelSmall BLDG_LIGHT_RESTROOM_SCH | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeSecondarySchool_RestroomInfil | SchoolSecondary INFIL_SCH_PNNL |  | 2.36 |  | Smooth | 0.0022 | 13.9 | 4190 | 878 | 0.9 | 0.7 | 0.7 | Mixed_Restroom_2mm | CalculatedEstimateStandardCommercialFixturesAndPartitionsMixed_Restroom_2mmInternalMassDef
CS Sales Area | 2021_WA_BuildingCode | Retail | Sales Area | 102 | 255 | 102 | CS Sales Area_2021WABuildingCode | CS Sales Area_2021WABuildingCodeScheduleSet | 0.16146 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - SalesCOMNET-REV9PeopleDef | NECB-C-Occupancy | CS Sales AreaActivity | 0.0035394 | 0.0006096 |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - SalesVent | 5.9124 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Sales AreaElectricalEquipDef | NECB-C-Electric-Equipment | 11.3022 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Sales areaLightingDef | NECB-C-Lighting | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeRetail_Point_of_SaleInfil | Always On |  | 3.54 |  | MediumRough | 0.0032 | 10.6 | 2496 | 1134 | 0.9 | 0.7 | 0.7 | Mixed_Retail_3mm | CalculatedEstimateDisplayShelvingAndMerchandiseInventoryMixed_Retail_3mmInternalMassDef
CS Seating Area General | 2021_WA_BuildingCode | Miscellaneous | Seating Area General | 230 | 196 | 120 | CS Seating Area General_2021WABuildingCode | CS Seating Area General_2021WABuildingCodeScheduleSet | 0.32292 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Lobbies/prefunctionCOMNET-REV9BA HotelPeopleDef | NECB-C-Occupancy | CS Seating Area GeneralActivity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Lobbies/prefunctionVent | 16.8363 | 0 | 0.5 | 0 | COMNET-REV9BA HotelWholeBuildingCS Seating Area GeneralElectricalEquipDef | NECB-C-Electric-Equipment | 2.4757 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Seating area, generalLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Transp. seatingInfil | Always On |  | 2.18 |  | MediumRough | 0.0063 | 6.65 | 1015 | 1349 | 0.9 | 0.7 | 0.7 | Mixed_Seating_6mm | CalculatedEstimateSofasChairsAndAreaRugMixed_Seating_6mmInternalMassDef
CS Stairway | 2021_WA_BuildingCode | Miscellaneous | Stairway | 230 | 157 | 120 | CS Stairway_2021WABuildingCode | CS Stairway_2021WABuildingCodeScheduleSet | [9 empty] | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Corridors serving other than Group R occupanciesVent | 3.2292 | 0 | 0.5 | 0 | COMNET-REV9BA WarehouseWholeBuildingCS StairwayElectricalEquipDef | HotelSmall AlwaysOff | 5.2744 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2StairwellLightingDef | HotelSmall BLDG_LIGHT_STAIR_SCH | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_StairwayInfil | Always On |  | 1.77 |  | MediumRough | 0.0188 | 9.97 | 3219 | 817 | 0.9 | 0.7 | 0.65 | Concrete_Stairway_19mm | CalculatedEstimateConcreteStairsWithHandrailsAndGuardrailsConcrete_Stairway_19mmInternalMassDef
CS Storage - Hospital | 2021_WA_BuildingCode | Hospital | Storage | 102 | 0 | 0 | CS Storage - Hospital_2021WABuildingCode | CS Storage - Hospital_2021WABuildingCodeScheduleSet | [9 empty] | 0.0006096 |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Storage roomsVent | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Storage - HospitalElectricalEquipDef | NECB-H-Electric-Equipment | 4.0903 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Storage room - All other storageLightingDef | NECB-H-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Storage areaInfil | Always On |  | 6.89 |  | Smooth | 0.0022 | 9.22 | 4416 | 928 | 0.9 | 0.7 | 0.7 | Steel_Hospital_Storage_2mm | CalculatedEstimateMedicalShelvingAndSupplyCartsSteel_Hospital_Storage_2mmInternalMassDef
CS Storage - >= 50 ft2 | 2021_WA_BuildingCode | Miscellaneous | Storage - >= 50 ft2 | 102 | 0 | 0 | CS Storage - >= 50 ft2 _2021WABuildingCode | CS Storage - >= 50 ft2 _2021WABuildingCodeScheduleSet | [9 empty] | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Storage - WarehousesVent | 3.3793 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Storage - >= 50 ft2 ElectricalEquipDef | NECB-E-Electric-Equipment | 4.0903 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Storage room - >= 50 ft2LightingDef | NECB-E-Lighting | [6 empty] | 1.3215e-05 | PNNL-90.1-2013DOE_PrototypeSmallHotel_Storage4FrontInfil | Always On |  | 7.37 |  | MediumRough | 0.004 | 10.9 | 2584 | 1123 | 0.9 | 0.7 | 0.7 | Mixed_Commercial_Storage_4mm | CalculatedEstimateShelvingWithFileAndPaperBoxesMixed_Commercial_Storage_4mmInternalMassDef
CS Storage - < 50 ft2 | 2021_WA_BuildingCode | Miscellaneous | Storage - < 50 ft2 | 102 | 0 | 0 | CS Storage - < 50 ft2 _2021WABuildingCode | CS Storage - < 50 ft2 _2021WABuildingCodeScheduleSet | [9 empty] | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Storage - WarehousesVent | 3.3793 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Storage - < 50 ft2 ElectricalEquipDef | NECB-E-Electric-Equipment | 5.4896 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Storage room - < 50 ft2LightingDef | NECB-E-Lighting | [6 empty] | 1.3215e-05 | PNNL-90.1-2013DOE_PrototypeSmallHotel_Storage4FrontInfil | Always On |  | 4.72 |  | MediumRough | 0.0025 | 14.7 | 2644 | 1128 | 0.9 | 0.7 | 0.7 | Mixed_Small_Storage_2mm | CalculatedEstimateWallShelvingInJanitorialClosetMixed_Small_Storage_2mmInternalMassDef
CS Vehicular Maintenance | 2021_WA_BuildingCode | Repair Garage | Vehicular Maintenance | 153 | 0 | 76 | CS Vehicular Maintenance_2021WABuildingCode | CS Vehicular Maintenance_2021WABuildingCodeScheduleSet | [11 empty] | Washington State Mechanical Code TABLE 403.3.1.1Storage_Repair garages_enclosed parking garageVent | 5.417 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeCS Vehicular MaintenanceElectricalEquipDef | NECB-A-Electric-Equipment | 6.4584 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Vehicular maintenanceLightingDef | NECB-A-Lighting | [6 empty] | 9.4389e-05 | EstimateSpace Function_Parking garage spaceInfil | Always On |  | 1.31 |  | Smooth | 0.0045 | 41.4 | 7054 | 551 | 0.9 | 0.7 | 0.7 | Steel_AutoShop_4mm | CalculatedEstimateVehicleLiftsAndToolChestsSteel_AutoShop_4mmInternalMassDef
CS Workshop | 2021_WA_BuildingCode | Workshop | Workshop | 160 | 160 | 160 | CS Workshop_2021WABuildingCode | CS Workshop_2021WABuildingCodeScheduleSet | 0.21528 | 468.9332 | 97 | 120 | 0.39688 | Washington State Mechanical Code TABLE 403.3.1.1Education - Wood/metal shopsCOMNET-REV9PeopleDef | NECB-A-Occupancy | CS WorkshopActivity | 0.0047192 | 0.0009144 |  | Washington State Mechanical Code TABLE 403.3.1.1Education - Wood/metal shopsVent | 4.6106 | 0.1 | 0.5 | 0.1 | COMNET-REV9EstimateCS WorkshopElectricalEquipDef | NECB-A-Electric-Equipment | 13.5626 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2WorkshopLightingDef | NECB-A-Lighting | [6 empty] | 9.4389e-05 | EstimateSpace Function_Parking garage spaceInfil | Always On |  | 2.27 |  | Smooth | 0.0025 | 40.8 | 6533 | 647 | 0.9 | 0.7 | 0.7 | Steel_Workshop_2mm | CalculatedEstimateMachineToolsAndWorkbenchesSteel_Workshop_2mmInternalMassDef
SS Assisted Living - Chapel | 2021_WA_BuildingCode | Religious | Chapel | 255 | 153 | 255 | SS Assisted Living - Chapel_2021WABuildingCode | SS Assisted Living - Chapel_2021WABuildingCodeScheduleSet | 1.2917 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Places of religious worshipCOMNET-REV9PeopleDef | NECB-C-Occupancy | SS Assisted Living - ChapelActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Places of religious worshipVent | 15.1196 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Assisted Living - ChapelElectricalEquipDef | NECB-C-Electric-Equipment | 7.5348 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Facility for the visually impaired - In a chapel (and not used primarily by the staff)LightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Religious - fellowship hallInfil | Always On |  | 3.06 |  | MediumRough | 0.008 | 3.09 | 855 | 1384 | 0.9 | 0.7 | 0.7 | Mixed_Chapel_8mm | CalculatedEstimateChapelSeatingAndAltarFurnishingsMixed_Chapel_8mmInternalMassDef
SS Assisted Living - Recreation Room | 2021_WA_BuildingCode | Assisted Living | Recreation Room | 255 | 0 | 0 | SS Assisted Living - Recreation Room_2021WABuildingCode | SS Assisted Living - Recreation Room_2021WABuildingCodeScheduleSet | 0.43056 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Health club/aerobics roomCOMNET-REV9PeopleDef | NECB-B-Occupancy | SS Assisted Living - Recreation RoomActivity | 0.0094384 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Health club/aerobics roomVent | 15.1196 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Assisted Living - Recreation RoomElectricalEquipDef | NECB-B-Electric-Equipment | 19.0523 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Facility for the visually impaired - In a recreation room (and not used primarily by the staff)LightingDef | NECB-B-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Hospital - lounge/recreationInfil | Always On |  | 3.38 |  | MediumRough | 0.0038 | 6.76 | 1572 | 1213 | 0.9 | 0.7 | 0.7 | Mixed_Recreation_4mm | CalculatedEstimateRecreationRoomFurnitureAndGameTablesMixed_Recreation_4mmInternalMassDef
SS Convention Center - Exhibit Space | 2021_WA_BuildingCode | Convention Center | Exhibit Space | 204 | 204 | 0 | SS Convention Center - Exhibit Space _2021WABuildingCode | SS Convention Center - Exhibit Space _2021WABuildingCodeScheduleSet | 0.43056 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Museums/galleriesCOMNET-REV9PeopleDef | NECB-C-Occupancy | SS Convention Center - Exhibit Space Activity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Museums/galleriesVent | 8.0473 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Convention Center - Exhibit Space ElectricalEquipDef | NECB-C-Electric-Equipment | 6.566 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Convention center - Exhibit spaceLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Convention centre - exhibitInfil | Always On |  | 2 |  | MediumRough | 0.0017 | 7.9 | 1757 | 1092 | 0.9 | 0.7 | 0.7 | Mixed_Exhibit_2mm | CalculatedEstimateConventionExhibitBoothsAndDisplaysMixed_Exhibit_2mmInternalMassDef
SS Dormitory - Living Quarters | 2021_WA_BuildingCode | Dormitory | Living Quarters | 176 | 224 | 230 | SS Dormitory - Living Quarters _2021WABuildingCode | SS Dormitory - Living Quarters _2021WABuildingCodeScheduleSet | 0.21528 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Dormitory sleeping areaCOMNET-REV9PeopleDef | NECB-G-Occupancy | SS Dormitory - Living Quarters Activity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Dormitory sleeping areaVent | 21.0558 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Dormitory - Living Quarters ElectricalEquipDef | NECB-G-Electric-Equipment | 5.382 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Dormitory living quartersLightingDef | NECB-G-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Dormitory - living quartersInfil | Always On |  | 4.15 |  | MediumRough | 0.0049 | 6.7 | 1266 | 1256 | 0.9 | 0.7 | 0.7 | Mixed_Dormitory_5mm | CalculatedEstimateDormitoryBedroomFurnitureMixed_Dormitory_5mmInternalMassDef
SS Fire Station - Sleeping Quarters | 2021_WA_BuildingCode | Fire Station | Sleeping Quarters | 176 | 224 | 230 | SS Fire Station - Sleeping Quarters _2021WABuildingCode | SS Fire Station - Sleeping Quarters _2021WABuildingCodeScheduleSet | 0.21528 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Dormitory sleeping areaCOMNET-REV9PeopleDef | NECB-G-Occupancy | SS Fire Station - Sleeping Quarters Activity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Hotels, motels, resorts and dormitories - Dormitory sleeping areaVent | 16.5804 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Fire Station - Sleeping Quarters ElectricalEquipDef | NECB-G-Electric-Equipment | 2.4757 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Fire stations - Sleeping quartersLightingDef | NECB-G-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Fire station - quartersInfil | Always On |  | 2.03 |  | Smooth | 0.0015 | 28.4 | 3803 | 996 | 0.9 | 0.7 | 0.7 | Steel_FireStation_2mm | CalculatedEstimateFireStationBunkAndLockerFurnitureSteel_FireStation_2mmInternalMassDef
SS Gymnasium/Fitness Center - Exercise Area | 2021_WA_BuildingCode | Gymnasium | Exercise Area | 255 | 0 | 0 | SS Gymnasium/Fitness Center - Exercise Area _2021WABuildingCode | SS Gymnasium/Fitness Center - Exercise Area _2021WABuildingCodeScheduleSet | 0.43056 | 527.5498 | 97 | 120 | 0.39444 | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Health club/aerobics roomCOMNET-REV9PeopleDef | NECB-B-Occupancy | SS Gymnasium/Fitness Center - Exercise Area Activity | 0.0094384 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Health club/aerobics roomVent | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Gymnasium/Fitness Center - Exercise Area ElectricalEquipDef | NECB-B-Electric-Equipment | 9.6876 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Gymnasium/fitness center - In an exercise areaLightingDef | NECB-B-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Gym - fitnessInfil | Always On |  | 1.79 |  | Smooth | 0.0024 | 50.2 | 6774 | 571 | 0.9 | 0.7 | 0.7 | Steel_Iron_Gym_2mm | CalculatedEstimateFreeWeightsAndExerciseEquipmentSteel_Iron_Gym_2mmInternalMassDef
SS Gymnasium/Fitness Center - Playing Area | 2021_WA_BuildingCode | Gymnasium | Playing Area | 255 | 0 | 0 | SS Gymnasium/Fitness Center - Playing Area _2021WABuildingCode | SS Gymnasium/Fitness Center - Playing Area _2021WABuildingCodeScheduleSet | 0.075347 | 527.5498 | 97 | 120 | 0.39444 | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Gym, stadium, arena (play area)COMNET-REV9PeopleDef | NECB-B-Occupancy | SS Gymnasium/Fitness Center - Playing Area Activity | 0.0094384 | 0.0009144 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Gym, stadium, arena (play area)Vent | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Gymnasium/Fitness Center - Playing Area ElectricalEquipDef | NECB-B-Electric-Equipment | 9.1494 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Gymnasium/fitness center - In a playing areaLightingDef | NECB-B-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Gym - fitnessInfil | Always On |  | 0.5 |  | Smooth | 0.0013 | 45.2 | 6107 | 662 | 0.9 | 0.7 | 0.7 | Steel_Gym_1mm | CalculatedEstimateGymnasiumPlayingFloorEquipmentSteel_Gym_1mmInternalMassDef
SS Healthcare - Emergency Room | 2021_WA_BuildingCode | Hospital | Emergency Room | 255 | 215 | 0 | SS Healthcare - Emergency Room_2021WABuildingCode | SS Healthcare - Emergency Room_2021WABuildingCodeScheduleSet | 0.21528 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care triage roomCOMNET-REV9PeopleDef | NECB-H-Occupancy | SS Healthcare - Emergency RoomActivity | 0.0047192 | 0.0009144 |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care triage roomVent | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Healthcare - Emergency RoomElectricalEquipDef | NECB-H-Electric-Equipment | 15.0696 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In an exam/treatment roomLightingDef | NECB-H-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Hospital - emergencyInfil | Always On |  | 1.89 |  | Smooth | 0.0011 | 24.8 | 4004 | 914 | 0.9 | 0.7 | 0.7 | Steel_Medical_1mm | CalculatedEstimateEmergencyRoomMedicalEquipmentSteel_Medical_1mmInternalMassDef
SS Healthcare - Exam/Treatment | 2021_WA_BuildingCode | Healthcare | Exam/Treatment | 136 | 78 | 222 | SS Healthcare - Exam/Treatment _2021WABuildingCode | SS Healthcare - Exam/Treatment _2021WABuildingCodeScheduleSet | 0.21528 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care treatment roomCOMNET-REV9PeopleDef | OutPatientHealthCare BLDG_OCC_SCH | SS Healthcare - Exam/Treatment Activity | 0.0035394 | 0.0009144 |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care treatment roomVent | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Healthcare - Exam/Treatment ElectricalEquipDef | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | 15.0696 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In an exam/treatment roomLightingDef | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeOutpatient_ExamInfil | OutPatientHealthCare INFIL_SCH |  | 2.3 |  | Smooth | 0.00094 | 30.3 | 4812 | 902 | 0.9 | 0.7 | 0.7 | Steel_MedExam_1mm | CalculatedEstimateExamTreatmentRoomEquipmentSteel_MedExam_1mmInternalMassDef
SS Healthcare - Supply Room | 2021_WA_BuildingCode | Healthcare | Supply Room | 0 | 128 | 128 | SS Healthcare - Supply Room_2021WABuildingCode | SS Healthcare - Supply Room_2021WABuildingCodeScheduleSet | [9 empty] | 0.0006096 |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Storage roomsVent | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Healthcare - Supply RoomElectricalEquipDef | NECB-H-Electric-Equipment | 6.6737 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In a medical supply roomLightingDef | NECB-H-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeHospital_Hospital - medical supplyInfil | Always On |  | 5.95 |  | Smooth | 0.0017 | 29.9 | 4600 | 860 | 0.9 | 0.7 | 0.7 | Steel_MedSupply_2mm | CalculatedEstimateMedicalSupplyShelvingAndCartsSteel_MedSupply_2mmInternalMassDef
SS Healthcare - Nursery | 2021_WA_BuildingCode | Healthcare | Nursery | 78 | 167 | 222 | SS Healthcare - Nursery _2021WABuildingCode | SS Healthcare - Nursery _2021WABuildingCodeScheduleSet | 0.21528 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care observation roomCOMNET-REV9PeopleDef | Hospital BLDG_OCC_EXTD_SCH | SS Healthcare - Nursery Activity | 0.0023596 | 0.0003048 |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care observation roomVent | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Healthcare - Nursery ElectricalEquipDef | Hospital BLDG_EQUIP_EXTD_SCH | 9.9029 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In a nurseryLightingDef | Hospital BLDG_LIGHT_EXTD_SCH | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeHospital_ICU_OpenInfil | Hospital INFIL_SCH_PNNL |  | 2.48 |  | Smooth | 0.0012 | 41.5 | 3996 | 921 | 0.9 | 0.7 | 0.7 | Steel_Nursery_1mm | CalculatedEstimateNurseryBassinetsAndEquipmentSteel_Nursery_1mmInternalMassDef
SS Healthcare - Nurses’ Station | 2021_WA_BuildingCode | Healthcare | Nurses’ Station | 31 | 162 | 169 | SS Healthcare - Nurses’ Station _2021WABuildingCode | SS Healthcare - Nurses’ Station _2021WABuildingCodeScheduleSet | 0.64583 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019Office Buildings - Telephone/data entryCOMNET-REV9PeopleDef | Hospital BLDG_OCC_SCH | SS Healthcare - Nurses’ Station Activity | 0.0023596 | 0.0003048 |  | ASHRAE 62.1-2019Office Buildings - Telephone/data entryVent | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Healthcare - Nurses’ Station ElectricalEquipDef | Hospital BLDG_EQUIP_SCH | 12.5939 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In a nurse's stationLightingDef | Hospital BLDG_LIGHT_NURSEFLR234_SCH | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeHospital_Hospital NurseStnInfil | Hospital INFIL_SCH_PNNL |  | 3.71 |  | MediumRough | 0.0015 | 20.2 | 3433 | 958 | 0.9 | 0.7 | 0.7 | Mixed_NurseStation_2mm | CalculatedEstimateNursesStationDeskAndEquipmentMixed_NurseStation_2mmInternalMassDef
SS Healthcare - Operating Room | 2021_WA_BuildingCode | Healthcare | Operating Room | 169 | 31 | 159 | SS Healthcare - Operating Room _2021WABuildingCode | SS Healthcare - Operating Room _2021WABuildingCodeScheduleSet | 0.21528 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019Outpatient Health Care Facilities - Dental operatoryCOMNET-REV9PeopleDef | Hospital BLDG_OCC_EXTD_SCH | SS Healthcare - Operating Room Activity | 0.0047192 | 0.0009144 |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Dental operatoryVent | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Healthcare - Operating Room ElectricalEquipDef | Hospital BLDG_EQUIP_EXTD_SCH | 24.3266 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In an operating roomLightingDef | Hospital BLDG_LIGHT_EXTD_SCH | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeHospital_Hospital ORInfil | Hospital INFIL_SCH_PNNL |  | 2.81 |  | Smooth | 0.0015 | 62.4 | 6305 | 596 | 0.9 | 0.7 | 0.7 | Steel_Aluminum_OR_2mm | CalculatedEstimateOperatingRoomStainlessEquipmentSteel_Aluminum_OR_2mmInternalMassDef
SS Healthcare - Patient Room | 2021_WA_BuildingCode | Healthcare | Patient Room | 78 | 167 | 222 | SS Healthcare - Patient Room _2021WABuildingCode | SS Healthcare - Patient Room _2021WABuildingCodeScheduleSet | 0.21528 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care observation roomCOMNET-REV9PeopleDef | Hospital BLDG_OCC_EXTD_SCH | SS Healthcare - Patient Room Activity | 0.0023596 | 0.0003048 |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care observation roomVent | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Healthcare - Patient Room ElectricalEquipDef | Hospital BLDG_EQUIP_SCH | 7.3195 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In a patient roomLightingDef | Hospital BLDG_LIGHT_SCH | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeHospital_Hospital PatRoomInfil | Hospital INFIL_SCH_PNNL |  | 1.22 |  | MediumRough | 0.0254 | 1.3 | 309 | 718 | 0.9 | 0.7 | 0.7 | Mixed_Healthcare_PatientRoom_25mm | CalculatedEstimatePatientRoomBedAndFurnishingsMixed_Healthcare_PatientRoom_25mmInternalMassDef
SS Healthcare - Physical Therapy | 2021_WA_BuildingCode | Healthcare | Physical Therapy | 154 | 230 | 120 | SS Healthcare - Physical Therapy _2021WABuildingCode | SS Healthcare - Physical Therapy _2021WABuildingCodeScheduleSet | 0.075347 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019Outpatient Health Care Facilities - Physical therapy exercise areaCOMNET-REV9PeopleDef | Hospital BLDG_OCC_SCH | SS Healthcare - Physical Therapy Activity | 0.0094384 | 0.0009144 |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Physical therapy exercise areaVent | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Healthcare - Physical Therapy ElectricalEquipDef | Hospital BLDG_EQUIP_SCH | 9.7952 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In a physical therapy roomLightingDef | Hospital BLDG_LIGHT_SCH | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeHospital_Hospital PhysTherapyInfil | Hospital INFIL_SCH_PNNL |  | 0.89 |  | MediumRough | 0.0166 | 4.21 | 847 | 581 | 0.9 | 0.7 | 0.7 | Mixed_Healthcare_PhysicalTherapy_17mm | CalculatedEstimatePhysicalTherapyEquipmentAndMatsMixed_Healthcare_PhysicalTherapy_17mmInternalMassDef
SS Healthcare - Recovery Room | 2021_WA_BuildingCode | Healthcare | Recovery Room | 169 | 31 | 159 | SS Healthcare - Recovery Room_2021WABuildingCode | SS Healthcare - Recovery Room_2021WABuildingCodeScheduleSet | 0.21528 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care observation roomCOMNET-REV9PeopleDef | OutPatientHealthCare BLDG_OCC_SCH | SS Healthcare - Recovery RoomActivity | 0.0023596 | 0.0003048 |  | ASHRAE 62.1-2019Outpatient Health Care Facilities - Urgent care observation roomVent | 13.4424 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Healthcare - Recovery RoomElectricalEquipDef | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | 13.455 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Health care facility - In a recovery roomLightingDef | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | [6 empty] | 2.1049e-05 | PNNL-90.1-2013DOE_PrototypeHospital_Outpatient PACUInfil | OutPatientHealthCare INFIL_SCH |  | 1.09 |  | MediumRough | 0.0109 | 4.21 | 957 | 661 | 0.9 | 0.7 | 0.7 | Mixed_Healthcare_RecoveryRoom_11mm | CalculatedEstimateRecoveryRoomBedAndMonitoringEquipmentMixed_Healthcare_RecoveryRoom_11mmInternalMassDef
SS Library - Reading Area | 2021_WA_BuildingCode | Library | Reading Area | 240 | 230 | 140 | SS Library - Reading Area _2021WABuildingCode | SS Library - Reading Area _2021WABuildingCodeScheduleSet | 0.10764 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - LibrariesCOMNET-REV9PeopleDef | NECB-C-Occupancy | SS Library - Reading Area Activity | 0.0023596 | 0.0006096 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - LibrariesVent | 10.0883 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Library - Reading Area ElectricalEquipDef | NECB-C-Electric-Equipment | 10.3334 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Library - In a reading areaLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Library - readingInfil | Always On |  | 1.54 |  | MediumRough | 0.0221 | 0.18 | 344 | 1399 | 0.9 | 0.7 | 0.7 | Mixed_Library_ReadingArea_22mm | CalculatedEstimateWoodTablesCarrelsAndSeatingMixed_Library_ReadingArea_22mmInternalMassDef
SS Library - Stacks | 2021_WA_BuildingCode | Library | Stacks | 218 | 165 | 32 | SS Library - Stacks _2021WABuildingCode | SS Library - Stacks _2021WABuildingCodeScheduleSet | 0.10764 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - LibrariesCOMNET-REV9PeopleDef | NECB-C-Occupancy | SS Library - Stacks Activity | 0.0023596 | 0.0006096 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - LibrariesVent | 10.0883 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Library - Stacks ElectricalEquipDef | NECB-C-Electric-Equipment | 11.8404 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Library - In the stacksLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Library - stacksInfil | Always On |  | 8.85 |  | MediumRough | 0.0122 | 1.707 | 1346 | 1140 | 0.9 | 0.7 | 0.7 | Mixed_Library_Stacks_12mm | CalculatedEstimateSteelShelvingWithBooksMixed_Library_Stacks_12mmInternalMassDef
SS Manufacturing Facility - Detailed Manufacturing | 2021_WA_BuildingCode | Manufacturing Facility | Detailed Manufacturing | 127 | 0 | 255 | SS Manufacturing Facility - Detailed Manufacturing _2021WABuildingCode | SS Manufacturing Facility - Detailed Manufacturing _2021WABuildingCodeScheduleSet | 0.075347 | 424.9707 | 97 | 120 | 0.4 | ASHRAE 62.1-2019Miscellaneous Spaces - Manufacturing where hazardous materials are not usedCOMNET-REV9PeopleDef | NECB-A-Occupancy | SS Manufacturing Facility - Detailed Manufacturing Activity | 0.0047192 | 0.0009144 |  | ASHRAE 62.1-2019Miscellaneous Spaces - Manufacturing where hazardous materials are not usedVent | 3.7116 | 0.1 | 0.5 | 0.1 | COMNET-REV9EstimateSS Manufacturing Facility - Detailed Manufacturing ElectricalEquipDef | NECB-A-Electric-Equipment | 8.6112 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Manufacturing facility - In a detailed manufacturing areaLightingDef | NECB-A-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Mfg - detailedInfil | Always On |  | 1.04 |  | MediumRough | 0.0116 | 40.35 | 6074 | 483 | 0.9 | 0.7 | 0.7 | Mixed_Manufacturing_Detailed_12mm | CalculatedEstimateCNCMachineToolsAndWorkbenchesMixed_Manufacturing_Detailed_12mmInternalMassDef
SS Manufacturing Facility - Equipment Room | 2021_WA_BuildingCode | Manufacturing Facility | Equipment Room | 41 | 31 | 175 | SS Manufacturing Facility - Equipment Room _2021WABuildingCode | SS Manufacturing Facility - Equipment Room _2021WABuildingCodeScheduleSet | 0.075347 | 424.9707 | 97 | 120 | 0.4 | Rule of ThumbRequires engineering analysis per Section 403.3.1.1COMNET-REV9PeopleDef | NECB-A-Occupancy | SS Manufacturing Facility - Equipment Room Activity |  |  | 6 | Rule of ThumbRequires engineering analysis per Section 403.3.1.1Vent | 3.7116 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Manufacturing Facility - Equipment Room ElectricalEquipDef | NECB-A-Electric-Equipment | 8.1806 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Manufacturing facility - In an equipment roomLightingDef | NECB-A-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Mfg - equipmentInfil | Always On |  | 0.76 |  | MediumRough | 0.0069 | 40.55 | 4978 | 548 | 0.9 | 0.7 | 0.7 | Mixed_Manufacturing_EquipRoom_7mm | CalculatedEstimateCompressorsHPUsAndElectricalPanelsMixed_Manufacturing_EquipRoom_7mmInternalMassDef
SS Manufacturing Facility - Extra High Bay (>50 ft Floor to Ceiling Height) | 2021_WA_BuildingCode | Manufacturing Facility | Extra High Bay (>50 ft Floor to Ceiling Height) | 102 | 0 | 204 | SS Manufacturing Facility - Extra High Bay (>50 ft Floor to Ceiling Height) _2021WABuildingCode | SS Manufacturing Facility - Extra High Bay (>50 ft Floor to Ceiling Height) _2021WABuildingCodeScheduleSet | 0.075347 | 424.9707 | 97 | 120 | 0.4 | ASHRAE 62.1-2019Miscellaneous Spaces - Manufacturing where hazardous materials are not used - ACHCOMNET-REV9PeopleDef | NECB-A-Occupancy | SS Manufacturing Facility - Extra High Bay (>50 ft Floor to Ceiling Height) Activity |  |  | 0.09 | ASHRAE 62.1-2019Miscellaneous Spaces - Manufacturing where hazardous materials are not usedACHVent | 3.7116 | 0.1 | 0.5 | 0.1 | COMNET-REV9EstimateSS Manufacturing Facility - Extra High Bay (>50 ft Floor to Ceiling Height) ElectricalEquipDef | NECB-A-Electric-Equipment | 15.2849 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Manufacturing facility - In an extra high bay area (> 50-foot floor-ceiling height)LightingDef | NECB-A-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Mfg - bay H > 15mInfil | Always On |  | 0.67 |  | MediumRough | 0.029 | 48.41 | 7474 | 463 | 0.9 | 0.7 | 0.7 | Mixed_Manufacturing_ExtraHighBay_29mm | CalculatedEstimateOverheadCranesAndHeavyPressesMixed_Manufacturing_ExtraHighBay_29mmInternalMassDef
SS Manufacturing Facility - High Bay (25–50 ft Floor to Ceiling Height) | 2021_WA_BuildingCode | Manufacturing Facility | High Bay (25–50 ft Floor to Ceiling Height) | 216 | 191 | 216 | SS Manufacturing Facility - High Bay (25–50 ft Floor to Ceiling Height) _2021WABuildingCode | SS Manufacturing Facility - High Bay (25–50 ft Floor to Ceiling Height) _2021WABuildingCodeScheduleSet | 0.075347 | 424.9707 | 97 | 120 | 0.4 | ASHRAE 62.1-2019Miscellaneous Spaces - Manufacturing where hazardous materials are not used - ACHCOMNET-REV9PeopleDef | NECB-A-Occupancy | SS Manufacturing Facility - High Bay (25–50 ft Floor to Ceiling Height) Activity |  |  | 0.09 | ASHRAE 62.1-2019Miscellaneous Spaces - Manufacturing where hazardous materials are not usedACHVent | 3.7116 | 0.1 | 0.5 | 0.1 | COMNET-REV9EstimateSS Manufacturing Facility - High Bay (25–50 ft Floor to Ceiling Height) ElectricalEquipDef | NECB-A-Electric-Equipment | 13.3474 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Manufacturing facility - In a high bay area (25 - 50-foot floor-ceiling height)LightingDef | NECB-A-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Mfg - 7.5 <= bay H <= 15mInfil | Always On |  | 0.93 |  | MediumRough | 0.0158 | 35.21 | 6079 | 611 | 0.9 | 0.7 | 0.7 | Mixed_Manufacturing_HighBay_16mm | CalculatedEstimateCranesCuttingTablesAndStorageRacksMixed_Manufacturing_HighBay_16mmInternalMassDef
SS Manufacturing Facility - Low Bay (<25 ft Floor to Ceiling Height) | 2021_WA_BuildingCode | Manufacturing Facility | Low Bay (<25 ft Floor to Ceiling Height) | 221 | 160 | 221 | SS Manufacturing Facility - Low Bay (<25 ft Floor to Ceiling Height) _2021WABuildingCode | SS Manufacturing Facility - Low Bay (<25 ft Floor to Ceiling Height) _2021WABuildingCodeScheduleSet | 0.075347 | 424.9707 | 97 | 120 | 0.4 | ASHRAE 62.1-2019Miscellaneous Spaces - Manufacturing where hazardous materials are not used - ACHCOMNET-REV9PeopleDef | NECB-A-Occupancy | SS Manufacturing Facility - Low Bay (<25 ft Floor to Ceiling Height) Activity |  |  | 0.09 | ASHRAE 62.1-2019Miscellaneous Spaces - Manufacturing where hazardous materials are not usedACHVent | 3.7116 | 0.1 | 0.5 | 0.1 | COMNET-REV9EstimateSS Manufacturing Facility - Low Bay (<25 ft Floor to Ceiling Height) ElectricalEquipDef | NECB-A-Electric-Equipment | 9.257 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Manufacturing facility - In a low bay area (< 25-foot floor-ceiling height)LightingDef | NECB-A-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Mfg - bay H < 7.5mInfil | Always On |  | 1.21 |  | MediumRough | 0.0121 | 41.22 | 5929 | 485 | 0.9 | 0.7 | 0.7 | Mixed_Manufacturing_LowBay_12mm | CalculatedEstimateStampingPressesAndInjectionMoldersMixed_Manufacturing_LowBay_12mmInternalMassDef
SS Museum - General Exhibition | 2021_WA_BuildingCode | Museum | General Exhibition | 204 | 204 | 0 | SS Museum - General Exhibition _2021WABuildingCode | SS Museum - General Exhibition _2021WABuildingCodeScheduleSet | 0.43056 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Museums/galleriesCOMNET-REV9PeopleDef | NECB-C-Occupancy | SS Museum - General Exhibition Activity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Museums/galleriesVent | 8.0176 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Museum - General Exhibition ElectricalEquipDef | NECB-C-Electric-Equipment | 3.3368 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Museum - In a general exhibition areaLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Museum - exhibitionInfil | Always On |  | 1.18 |  | MediumRough | 0.0133 | 5.26 | 846 | 1136 | 0.9 | 0.7 | 0.7 | Mixed_Museum_Exhibition_13mm | CalculatedEstimateDisplayCasesAndPedestalsMixed_Museum_Exhibition_13mmInternalMassDef
SS Museum - Restoration | 2021_WA_BuildingCode | Museum | Restoration | 160 | 160 | 160 | SS Museum - Restoration _2021WABuildingCode | SS Museum - Restoration _2021WABuildingCodeScheduleSet | 0.43056 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019Public Assembly Spaces - Museums (children’s)COMNET-REV9PeopleDef | NECB-A-Occupancy | SS Museum - Restoration Activity | 0.0035394 | 0.0006096 |  | ASHRAE 62.1-2019Public Assembly Spaces - Museums (children’s)Vent | 4.6106 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Museum - Restoration ElectricalEquipDef | NECB-A-Electric-Equipment | 11.8404 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Museum - In a restoration roomLightingDef | NECB-A-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Museum - restorationInfil | Always On |  | 1.65 |  | MediumRough | 0.0058 | 12.26 | 2395 | 642 | 0.9 | 0.6 | 0.6 | Mixed_Museum_Restoration_6mm | CalculatedEstimateSteelCaseworkHoodsAndHardwoodBenchesMixed_Museum_Restoration_6mmInternalMassDef
SS Post Office - Sorting Area | 2021_WA_BuildingCode | Post Office | Sorting Area | 245 | 245 | 220 | SS Post Office - Sorting Area _2021WABuildingCode | SS Post Office - Sorting Area _2021WABuildingCodeScheduleSet | 0.075347 | 131.8875 | 97 | 120 | 0.55556 | ASHRAE 62.1-2019Miscellaneous Spaces - Sorting, packing, light assemblyCOMNET-REV9PeopleDef | NECB-A-Occupancy | SS Post Office - Sorting Area Activity | 0.0035394 | 0.0006096 |  | ASHRAE 62.1-2019Miscellaneous Spaces - Sorting, packing, light assemblyVent | 17.9649 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Post Office - Sorting Area ElectricalEquipDef | NECB-A-Electric-Equipment | 8.1806 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Post office - Sorting areaLightingDef | NECB-A-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Post office sortingInfil | Always On |  | 3.09 |  | MediumRough | 0.0016 | 42.18 | 6314 | 491 | 0.9 | 0.7 | 0.7 | Mixed_PostOffice_SortingArea_2mm | CalculatedEstimateFlatSortCasesAndMailHampersMixed_PostOffice_SortingArea_2mmInternalMassDef
SS Religious Building - Fellowship Hall | 2021_WA_BuildingCode | Religious | Fellowship Hall | 255 | 153 | 255 | SS Religious Building - Fellowship Hall_2021WABuildingCode | SS Religious Building - Fellowship Hall_2021WABuildingCodeScheduleSet | 1.2917 | 117.2333 | 97 | 120 | 0.6125 | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Places of religious worshipCOMNET-REV9PeopleDef | NECB-C-Occupancy | SS Religious Building - Fellowship HallActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Places of religious worshipVent | 3.2125 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Religious Building - Fellowship HallElectricalEquipDef | NECB-C-Electric-Equipment | 5.8126 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Religious building - In a fellowship hallLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Religious - fellowship hallInfil | Always On |  | 1.15 |  | MediumRough | 0.0073 | 2.614 | 902 | 1157 | 0.9 | 0.7 | 0.7 | Mixed_ReligiousBuilding_FellowshipHall_7mm | CalculatedEstimateFoldingTablesAndStackableChairsMixed_ReligiousBuilding_FellowshipHall_7mmInternalMassDef
SS Religious Building - Worship/Pulpit/Choir | 2021_WA_BuildingCode | Religious | Worship/Pulpit/Choir | 255 | 153 | 255 | SS Religious Building - Worship/Pulpit/Choir_2021WABuildingCode | SS Religious Building - Worship/Pulpit/Choir_2021WABuildingCodeScheduleSet | 1.2917 | 117.2333 | 97 | 120 | 0.6125 | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Places of religious worshipCOMNET-REV9PeopleDef | NECB-I-Occupancy | SS Religious Building - Worship/Pulpit/ChoirActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Public spaces - Places of religious worshipVent | 3.2125 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Religious Building - Worship/Pulpit/ChoirElectricalEquipDef | NECB-I-Electric-Equipment | 9.1494 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Religious building - In a worship pulpit/choir areaLightingDef | NECB-I-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Religious - pulpit/choirInfil | Always On |  | 0.88 |  | MediumRough | 0.0208 | 0.251 | 721 | 1568 | 0.9 | 0.7 | 0.7 | Mixed_ReligiousBuilding_WorshipChoir_21mm | CalculatedEstimateSolidHardwoodPewsAndPulpitMixed_ReligiousBuilding_WorshipChoir_21mmInternalMassDef
SS Retail - Dressing/Fitting Room | 2021_WA_BuildingCode | Retail | Dressing/Fitting Room | 230 | 230 | 250 | SS Retail - Dressing/Fitting Room _2021WABuildingCode | SS Retail - Dressing/Fitting Room _2021WABuildingCodeScheduleSet | [11 empty] | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Dressing roomsVent | 8.8434 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Retail - Dressing/Fitting Room ElectricalEquipDef | NECB-C-Electric-Equipment | 5.4896 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Retail - In a dressing/fitting roomLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Retail - dressing/fittingInfil | Always On |  | 3.91 |  | MediumRough | 0.0092 | 0.668 | 773 | 1222 | 0.9 | 0.7 | 0.7 | Mixed_Retail_DressingRoom_9mm | CalculatedEstimateMDFStallPartitionsAndMirrorsMixed_Retail_DressingRoom_9mmInternalMassDef
SS Retail - Mall Concourse | 2021_WA_BuildingCode | Retail | Mall Concourse | 176 | 196 | 222 | SS Retail - Mall Concourse _2021WABuildingCode | SS Retail - Mall Concourse _2021WABuildingCodeScheduleSet | 0.43056 | 131.8875 | 97 | 120 | 0.55556 | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Mall common areasCOMNET-REV9PeopleDef | NECB-C-Occupancy | SS Retail - Mall Concourse Activity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Mall common areasVent | 0 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Retail - Mall Concourse ElectricalEquipDef | NECB-C-Electric-Equipment | 8.8265 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Retail - In a mall concourseLightingDef | NECB-C-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Retail - mall concourseInfil | Always On |  | 0.4 |  | MediumRough | 0.0192 | 5.444 | 1338 | 1154 | 0.9 | 0.7 | 0.7 | Mixed_Retail_MallConcourse_19mm | CalculatedEstimateKiosksBenchesAndConcretePlantersMixed_Retail_MallConcourse_19mmInternalMassDef
SS Sports Arena Playing Area - Class I | 2021_WA_BuildingCode | Sports Arena | Playing Area - Class I | 127 | 255 | 212 | SS Sports Arena Playing Area - Class I _2021WABuildingCode | SS Sports Arena Playing Area - Class I _2021WABuildingCodeScheduleSet | 1.6146 | 102.5791 | 97 | 120 | 0.7 | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Spectator areasCOMNET-REV9PeopleDef | NECB-B-Occupancy | SS Sports Arena Playing Area - Class I Activity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Spectator areasVent | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Sports Arena Playing Area - Class I ElectricalEquipDef | NECB-B-Electric-Equipment | 31.6462 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Sports arena - Playing area - For a Class 1 facilityLightingDef | NECB-B-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Sports arena - court c1Infil | Always On |  | 0.23 |  | MediumRough | 0.0216 | 3.077 | 438 | 1165 | 0.9 | 0.7 | 0.7 | Mixed_SportsArena_PlayingArea_22mm | CalculatedEstimatePortableGoalsAndBenchesClassIMixed_SportsArena_PlayingArea_22mmInternalMassDef
SS Sports Arena Playing Area - Class II | 2021_WA_BuildingCode | Sports Arena | Playing Area - Class II | 176 | 224 | 230 | SS Sports Arena Playing Area - Class II _2021WABuildingCode | SS Sports Arena Playing Area - Class II _2021WABuildingCodeScheduleSet | 1.6146 | 102.5791 | 97 | 120 | 0.7 | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Spectator areasCOMNET-REV9PeopleDef | NECB-B-Occupancy | SS Sports Arena Playing Area - Class II Activity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Spectator areasVent | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Sports Arena Playing Area - Class II ElectricalEquipDef | NECB-B-Electric-Equipment | 21.6356 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Sports arena - Playing area - For a Class 2 facilityLightingDef | NECB-B-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Sports arena - court c2Infil | Always On |  | 0.23 |  | MediumRough | 0.0216 | 3.077 | 438 | 1165 | 0.9 | 0.7 | 0.7 | Mixed_SportsArena_PlayingArea_22mm | CalculatedEstimatePortableGoalsAndBenchesClassIIMixed_SportsArena_PlayingArea_22mmInternalMassDef
SS Sports Arena Playing Area - Class III | 2021_WA_BuildingCode | Sports Arena | Playing Area - Class III | 70 | 130 | 180 | SS Sports Arena Playing Area - Class III _2021WABuildingCode | SS Sports Arena Playing Area - Class III _2021WABuildingCodeScheduleSet | 1.6146 | 102.5791 | 97 | 120 | 0.7 | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Spectator areasCOMNET-REV9PeopleDef | NECB-B-Occupancy | SS Sports Arena Playing Area - Class III Activity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Spectator areasVent | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Sports Arena Playing Area - Class III ElectricalEquipDef | NECB-B-Electric-Equipment | 13.9932 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Sports arena - Playing area - For a Class 3 facilityLightingDef | NECB-B-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Sports arena - court c3Infil | Always On |  | 0.23 |  | MediumRough | 0.0216 | 3.077 | 438 | 1165 | 0.9 | 0.7 | 0.7 | Mixed_SportsArena_PlayingArea_22mm | CalculatedEstimatePortableGoalsAndBenchesClassIIIMixed_SportsArena_PlayingArea_22mmInternalMassDef
SS Sports Arena Playing Area - Class IV | 2021_WA_BuildingCode | Sports Arena | Playing Area - Class IV | 0 | 191 | 255 | SS Sports Arena Playing Area - Class IV_2021WABuildingCode | SS Sports Arena Playing Area - Class IV_2021WABuildingCodeScheduleSet | 1.6146 | 102.5791 | 97 | 120 | 0.7 | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Spectator areasCOMNET-REV9PeopleDef | NECB-B-Occupancy | SS Sports Arena Playing Area - Class IVActivity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Sports and amusement - Spectator areasVent | 7.2576 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Sports Arena Playing Area - Class IVElectricalEquipDef | NECB-B-Electric-Equipment | 9.257 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Sports arena - Playing area - For a Class 4 facilityLightingDef | NECB-B-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Sports arena - court c4Infil | Always On |  | 0.23 |  | MediumRough | 0.0216 | 3.077 | 438 | 1165 | 0.9 | 0.7 | 0.7 | Mixed_SportsArena_PlayingArea_22mm | CalculatedEstimatePortableGoalsAndBenchesClassIVMixed_SportsArena_PlayingArea_22mmInternalMassDef
SS Transportation - Baggage/Carousel Area | 2021_WA_BuildingCode | Transportation Facility | Baggage/Carousel Area | 135 | 206 | 250 | SS Transportation - Baggage/Carousel Area _2021WABuildingCode | SS Transportation - Baggage/Carousel Area _2021WABuildingCodeScheduleSet | 1.0764 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1Transportation - Transportation waitingCOMNET-REV9PeopleDef | NECB-H-Occupancy | SS Transportation - Baggage/Carousel Area Activity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Transportation - Transportation waitingVent | 8.2048 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Transportation - Baggage/Carousel Area ElectricalEquipDef | NECB-H-Electric-Equipment | 4.198 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Transportation - In a baggage/carousel areaLightingDef | NECB-H-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Transp. baggageInfil | Always On |  | 0.98 |  | MediumRough | 0.0045 | 37.62 | 3363 | 670 | 0.9 | 0.7 | 0.7 | Mixed_Transportation_BaggageCarousel_5mm | CalculatedEstimateCarouselsAndBaggageCartsMixed_Transportation_BaggageCarousel_5mmInternalMassDef
SS Transportation - Concourse | 2021_WA_BuildingCode | Transportation Facility | Concourse | 138 | 43 | 226 | SS Transportation - Concourse_2021WABuildingCode | SS Transportation - Concourse_2021WABuildingCodeScheduleSet | 1.0764 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1Transportation - Transportation waitingCOMNET-REV9PeopleDef | NECB-H-Occupancy | SS Transportation - ConcourseActivity | 0.0035394 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Transportation - Transportation waitingVent | 8.2048 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Transportation - ConcourseElectricalEquipDef | NECB-H-Electric-Equipment | 2.691 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Transportation - In an airport concourseLightingDef | NECB-H-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Transp. concourseInfil | Always On |  | 0.37 |  | MediumRough | 0.005 | 35.72 | 2081 | 857 | 0.9 | 0.7 | 0.7 | Mixed_Transportation_Concourse_5mm | CalculatedEstimateGateSeatingKiosksAndWalkwayMixed_Transportation_Concourse_5mmInternalMassDef
SS Transportation - Ticket Counter | 2021_WA_BuildingCode | Transportation Facility | Ticket Counter | 32 | 178 | 170 | SS Transportation - Ticket Counter_2021WABuildingCode | SS Transportation - Ticket Counter_2021WABuildingCodeScheduleSet | 0.64583 | 96.7175 | 97 | 120 | 0.68182 | Washington State Mechanical Code TABLE 403.3.1.1Theaters - Ticket boothsCOMNET-REV9PeopleDef | NECB-H-Occupancy | SS Transportation - Ticket CounterActivity | 0.0023596 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Theaters - Ticket boothsVent | 8.2048 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Transportation - Ticket CounterElectricalEquipDef | NECB-H-Electric-Equipment | 5.4896 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Transportation - At a terminal ticket counterLightingDef | NECB-H-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Transp. counterInfil | Always On |  | 1.07 |  | MediumRough | 0.0105 | 5.172 | 1374 | 952 | 0.9 | 0.7 | 0.7 | Mixed_Transportation_TicketCounter_11mm | CalculatedEstimateGraniteCountersAndQueueStanchionsMixed_Transportation_TicketCounter_11mmInternalMassDef
SS Warehouse - Medium/Bulky Items on Pallets | 2021_WA_BuildingCode | Warehouse | Medium/Bulky Items on Pallets | 220 | 20 | 60 | SS Warehouse - Medium/Bulky Items on Pallets_2021WABuildingCode | SS Warehouse - Medium/Bulky Items on Pallets_2021WABuildingCodeScheduleSet | [8 empty] | 0.0047192 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Warehouses (see Storage)Vent | 3.3793 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Warehouse - Medium/Bulky Items on PalletsElectricalEquipDef | NECB-A-Electric-Equipment | 3.5521 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Warehouse - Storage area - For medium to bulky palletized itemsLightingDef | NECB-A-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Warehouse - med/blkInfil | Always On |  | 1.15 |  | MediumRough | 0.0464 | 2.789 | 1088 | 1158 | 0.9 | 0.7 | 0.7 | Mixed_Warehouse_PalletItems_46mm | CalculatedEstimatePalletRackingAndStoredGoodsMixed_Warehouse_PalletItems_46mmInternalMassDef
SS Warehouse - Smaller Hand Carried Items | 2021_WA_BuildingCode | Warehouse | Smaller Hand Carried Items | 255 | 160 | 122 | SS Warehouse - Smaller Hand Carried Items_2021WABuildingCode | SS Warehouse - Smaller Hand Carried Items_2021WABuildingCodeScheduleSet | [8 empty] | 0.0047192 | 0.0003048 |  | Washington State Mechanical Code TABLE 403.3.1.1Retail stores, sales floors, and showroom floors - Warehouses (see Storage)Vent | 3.3793 | 0 | 0.5 | 0 | COMNET-REV9DOEPrototypeSS Warehouse - Smaller Hand Carried ItemsElectricalEquipDef | NECB-A-Electric-Equipment | 7.4272 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Warehouse - Storage area - For smaller, hand-carried itemsLightingDef | NECB-A-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Warehouse - fineInfil | Always On |  | 1.92 |  | MediumRough | 0.0101 | 4.073 | 1303 | 1027 | 0.9 | 0.7 | 0.7 | Mixed_Warehouse_HandCarryItems_10mm | CalculatedEstimateBoltlessShelvingAndBinStorageMixed_Warehouse_HandCarryItems_10mmInternalMassDef
CS Food Preparation - Electric Cooking | 2021_WA_BuildingCode | Commercial Kitchen | Food Preparation - Electric Cooking | 255 | 178 | 102 | CS Food Preparation - Electric Cooking_2021WABuildingCode | CS Food Preparation - Electric Cooking_2021WABuildingCodeScheduleSet | 0.21528 | 161.1958 | 97 | 120 | 0.5 | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Kitchens (cooking)COMNET-REV9PeopleDef | NECB-B-Occupancy | CS Food Preparation - Electric CookingActivity | 0.0035394 | 0.0006096 |  | Washington State Mechanical Code TABLE 403.3.1.1Food and beverage service_Kitchens (cooking)Vent | 110.6324 | 0.25 | 0.3 | 0.2 | COMNET-REV9California Commercial End-Use Survey (CEUS)DOEPrototypeCS Food Preparation - Electric CookingElectricalEquipDef | NECB-B-Electric-Equipment | 11.7328 | 0.37 | 0.2 | Washington State Energy Code Commercial TABLE C405.4.2Food preparationLightingDef | NECB-B-Lighting | [6 empty] | 2.3232e-05 | PNNL-NECB 2011DOE_PrototypeSpace Function_Food preparationInfil | Always On |  | 1.6 |  | MediumRough | 0.0063 | 16.8 | 2640 | 512 | 0.9 | 0.7 | 0.7 | Mixed_FoodPrep_ElectricCooking_6mm | CalculatedEstimateCommercialKitchenEquipmentSameAsGasCookingMixed_FoodPrep_ElectricCooking_6mmInternalMassDef

## Schedules
Each row represents the efficiency standards for a specificy type of chiller
Day Type choices: Default, Wkdy, Wknd, Mon, Tue, Wed, Thu, Fri, Sat, Sun, WntrDsn, SmrDsn, Hol
Name | Category | Units | Day Types | Start Date | End Date | Type | Hr 1 | Hr 2 | Hr 3 | Hr 4 | Hr 5 | Hr 6 | Hr 7 | Hr 8 | Hr 9 | Hr 10 | Hr 11 | Hr 12 | Hr 13 | Hr 14 | Hr 15 | Hr 16 | Hr 17 | Hr 18 | Hr 19 | Hr 20 | Hr 21 | Hr 22 | Hr 23 | Hr 24 | Notes
Always Off | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
Always Off | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
Always Off | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.4 | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 23.9 | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.4 | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.4 | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Always Off | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 22 | From DOE Prototype Buildings
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29 | From DOE Prototype Buildings
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Always On | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | bar: Hr 1 to Hr 24
ApartmentHighRise COMPACT HVAC-ALWAYS 4 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
ApartmentHighRise ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
ApartmentHighRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
ApartmentHighRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
ApartmentHighRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
ApartmentHighRise EQP_APT_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58 | From DOE Prototype Buildings
ApartmentHighRise EQP_OFF_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.33 | From DOE Prototype Buildings
ApartmentHighRise EQP_OFF_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | From DOE Prototype Buildings
ApartmentHighRise Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
ApartmentHighRise Exterior_Ltg_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_DESIGN_OFF_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_No_Optimum | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_No_Optimum | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_Yes_Optimum | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_Yes_Optimum | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentHighRise INF_APT_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
ApartmentHighRise INF_COR_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
ApartmentHighRise INF_OFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
ApartmentHighRise INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0 | From DOE Prototype Buildings
ApartmentHighRise LTG_APT_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.06 | 0.13 | 0.14 | 0.13 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.14 | 0.2 | 0.27 | 0.32 | 0.32 | 0.22 | 0.12 | 0.05 | From DOE Prototype Buildings
ApartmentHighRise LTG_COR_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
ApartmentHighRise LTG_OFF_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.18 | From DOE Prototype Buildings
ApartmentHighRise LTG_OFF_SCH | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
ApartmentHighRise LTG_OFF_SCH | Unknown |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | From DOE Prototype Buildings
ApartmentHighRise LTG_OFF_SCH | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentHighRise N CLGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentHighRise N HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentHighRise OCC_APT_SCH | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1 | From DOE Prototype Buildings
ApartmentHighRise OCC_OFF_SCH | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentHighRise OCC_OFF_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
ApartmentHighRise PLANT LOOP HIGH TEMP SCHEDULE | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
ApartmentHighRise PLANT LOOP LOW TEMP SCHEDULE | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 20 | From DOE Prototype Buildings
ApartmentHighRise PLANTCOOLINGONSCHED | Unknown |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
ApartmentHighRise PLANTCOOLINGONSCHED | Unknown |  | Wknd¦Wkdy | 2014-10-18 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentHighRise PLANTCOOLINGONSCHED | Unknown |  | Wknd¦Wkdy | 2014-01-01 | 2014-05-08 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentHighRise PLANTCOOLINGONSCHED | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentHighRise PLANTHEATINGONSCHED | Unknown |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentHighRise PLANTHEATINGONSCHED | Unknown |  | Wknd¦Wkdy | 2014-10-18 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
ApartmentHighRise PLANTHEATINGONSCHED | Unknown |  | Wknd¦Wkdy | 2014-01-01 | 2014-05-08 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
ApartmentHighRise PLANTHEATINGONSCHED | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
ApartmentHighRise PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
ApartmentHighRise S CLGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentHighRise S HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentHighRise SHW Latent fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
ApartmentHighRise SHW Sensible fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
ApartmentHighRise SHW SUPPLY TEMP SCHED | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
ApartmentHighRise SHW TARGET TEMP SCHED | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
ApartmentHighRise SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 22 | From DOE Prototype Buildings
ApartmentHighRise SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
ApartmentHighRise SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
ApartmentHighRise Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
ApartmentHighRise Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentHighRise SupplyFanSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
ApartmentHighRise ZONE CONTROL TYPE SCHED | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentHighRise ZONE CONTROL TYPE SCHED | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 2 | From DOE Prototype Buildings
ApartmentHighRise ZONE CONTROL TYPE SCHED | Unknown |  | Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
ApartmentHighRise ZONE CONTROL TYPE SCHED | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
ApartmentMidRise All Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentMidRise All On | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
ApartmentMidRise APT_DHW_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29 | From DOE Prototype Buildings
ApartmentMidRise BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
ApartmentMidRise BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
ApartmentMidRise BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.4 | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_No_Setback | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 23.9 | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_No_Setback | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.4 | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
ApartmentMidRise COMPACT HVAC-ALWAYS 0 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentMidRise COMPACT HVAC-ALWAYS 1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
ApartmentMidRise COMPACT HVAC-ALWAYS 18.3333338190008 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 18.3333 | From DOE Prototype Buildings
ApartmentMidRise COMPACT HVAC-ALWAYS 4 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
ApartmentMidRise Constant Mains Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 12 | From DOE Prototype Buildings
ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
ApartmentMidRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
ApartmentMidRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
ApartmentMidRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
ApartmentMidRise EQP_APT_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58 | From DOE Prototype Buildings
ApartmentMidRise EQP_OFF_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.33 | From DOE Prototype Buildings
ApartmentMidRise EQP_OFF_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | From DOE Prototype Buildings
ApartmentMidRise Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
ApartmentMidRise Exterior_Ltg_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
ApartmentMidRise Hot Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentMidRise INF_APT_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
ApartmentMidRise INF_COR_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
ApartmentMidRise INF_OFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
ApartmentMidRise INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0 | From DOE Prototype Buildings
ApartmentMidRise LTG_APT_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.06 | 0.13 | 0.14 | 0.13 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.14 | 0.2 | 0.27 | 0.32 | 0.32 | 0.22 | 0.12 | 0.05 | From DOE Prototype Buildings
ApartmentMidRise LTG_COR_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
ApartmentMidRise LTG_OFF_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.18 | From DOE Prototype Buildings
ApartmentMidRise LTG_OFF_SCH | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
ApartmentMidRise LTG_OFF_SCH | Unknown |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | From DOE Prototype Buildings
ApartmentMidRise LTG_OFF_SCH | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentMidRise N CLGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentMidRise N HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentMidRise OCC_APT_SCH | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1 | From DOE Prototype Buildings
ApartmentMidRise OCC_OFF_SCH | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentMidRise OCC_OFF_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
ApartmentMidRise S CLGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentMidRise S HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
ApartmentMidRise Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
ApartmentMidRise Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
FullServiceRestaurant Bldg Equip | Equipment |  | Default¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
FullServiceRestaurant Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.35 | From DOE Reference Buildings
FullServiceRestaurant Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
FullServiceRestaurant Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | From DOE Reference Buildings
FullServiceRestaurant Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
FullServiceRestaurant Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
FullServiceRestaurant Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | From DOE Reference Buildings
FullServiceRestaurant Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35 | From DOE Reference Buildings
FullServiceRestaurant Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
FullServiceRestaurant Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2 | From DOE Reference Buildings
FullServiceRestaurant Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
FullServiceRestaurant Bldg Swh | Service Water Heating |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | From DOE Reference Buildings
FullServiceRestaurant Bldg Swh | Service Water Heating |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | From DOE Reference Buildings
FullServiceRestaurant Bldg Swh | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | From DOE Reference Buildings
FullServiceRestaurant ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Reference Buildings
FullServiceRestaurant ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Reference Buildings
FullServiceRestaurant ClgSetp Kitchen | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Reference Buildings
FullServiceRestaurant ClgSetp Kitchen | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Reference Buildings
FullServiceRestaurant Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
FullServiceRestaurant Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
FullServiceRestaurant Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
FullServiceRestaurant Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
FullServiceRestaurant Gas Equip | Equipment |  | Default¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | From DOE Reference Buildings
FullServiceRestaurant Gas Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.25 | From DOE Reference Buildings
FullServiceRestaurant Gas Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
FullServiceRestaurant HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | From DOE Reference Buildings
FullServiceRestaurant HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Reference Buildings
FullServiceRestaurant HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Reference Buildings
FullServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | From DOE Reference Buildings
FullServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Reference Buildings
FullServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 19 | From DOE Reference Buildings
FullServiceRestaurant Infil Half On | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
FullServiceRestaurant Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Hospital AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital Bldg ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Reference Buildings
Hospital Bldg ClgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 25 | From DOE Reference Buildings
Hospital Bldg ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Reference Buildings
Hospital BLDG ELEVATORS | Elevator |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | From DOE Reference Buildings
Hospital BLDG ELEVATORS | Elevator |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Reference Buildings
Hospital BLDG ELEVATORS | Elevator |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Reference Buildings
Hospital Bldg Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Hospital Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Hospital Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Hospital Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.3 | From DOE Reference Buildings
Hospital Bldg HtgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Reference Buildings
Hospital Bldg HtgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 18.3 | From DOE Reference Buildings
Hospital Bldg HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Reference Buildings
Hospital Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Reference Buildings
Hospital Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Hospital Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Hospital Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Hospital Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Hospital Bldg Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
Hospital Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Hospital Bldg Occ | Occupancy |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Hospital BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital BLDG_ELEVATORS | Elevator |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital BLDG_ELEVATORS | Elevator |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_EXTD_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_EXTD_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_EXTD_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital BLDG_EQUIP_EXTD_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_EXTD_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXAM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXAM_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXAM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital BLDG_LIGHT_EXAM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXAM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXTD_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXTD_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXTD_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital BLDG_LIGHT_EXTD_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXTD_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital BLDG_OA_FRAC_SCH | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital BLDG_OA_FRAC_SCH | OA Air |  | WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_OCC_EXTD_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_OCC_EXTD_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_OCC_EXTD_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital BLDG_OCC_EXTD_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_OCC_EXTD_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital BLDG_SWH_EXTD_SCH | Service Water Heating |  | Default¦WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
Hospital BLDG_SWH_EXTD_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
Hospital BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital CLGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
Hospital Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Hospital Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
Hospital Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Hospital Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
Hospital CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
Hospital CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital Cool-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 12.8 | From DOE Prototype Buildings
Hospital Critical ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 22.2 | From DOE Reference Buildings
Hospital Critical Equip | Equipment |  | Default¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
Hospital Critical Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.3 | From DOE Reference Buildings
Hospital Critical HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.1 | From DOE Reference Buildings
Hospital Critical Light | Lighting |  | Default¦WntrDsn¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | From DOE Reference Buildings
Hospital Critical Occ | Occupancy |  | Default¦WntrDsn¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | From DOE Reference Buildings
Hospital CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 6.7 | From DOE Prototype Buildings
Hospital Dishwashing Booster Setpoint Temp Schedule | Service Water Heating | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 82.22 | From DOE Prototype Buildings
Hospital Dishwashing Booster Water Inlet Temp Schedule | Service Water Heating | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
Hospital ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital ER_Exam1_Mult4_Flr_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital ER_Exam1_Mult4_Flr_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital ER_Exam1_Mult4_Flr_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital ER_Exam1_Mult4_Flr_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital ER_Exam3_Mult4_Flr_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital ER_Exam3_Mult4_Flr_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital ER_Exam3_Mult4_Flr_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital ER_Exam3_Mult4_Flr_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital ER_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital ER_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital ER_Trauma1_Flr_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital ER_Trauma1_Flr_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital ER_Trauma1_Flr_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital ER_Trauma1_Flr_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital ER_Trauma2_Flr_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital ER_Trauma2_Flr_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital ER_Trauma2_Flr_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital ER_Trauma2_Flr_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital ER_Triage_Mult4_Flr_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital ER_Triage_Mult4_Flr_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital ER_Triage_Mult4_Flr_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital ER_Triage_Mult4_Flr_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital Heat-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 12.8 | From DOE Prototype Buildings
Hospital Hours_of_operation | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital HTGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
Hospital Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 50 | From DOE Prototype Buildings
Hospital HVACOperationSchd | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 82 | From DOE Prototype Buildings
Hospital ICU_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital ICU_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital Infil Quarter On | Infiltration |  | Default¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.25 | From DOE Reference Buildings
Hospital Infil Quarter On | Infiltration |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Hospital INFIL_SCH_PNNL | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.25 | From DOE Prototype Buildings
Hospital Kitchen ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
Hospital Kitchen ClgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Reference Buildings
Hospital Kitchen ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
Hospital Kitchen Exhaust | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Hospital Kitchen Exhaust | Equipment |  | Wknd | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Hospital Kitchen Exhaust | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Hospital Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | From DOE Prototype Buildings
Hospital Kitchen Gas | Equipment |  | Default¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | From DOE Reference Buildings
Hospital Kitchen Gas | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.25 | From DOE Reference Buildings
Hospital Kitchen Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Hospital Kitchen HtgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Hospital Kitchen HtgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Reference Buildings
Hospital Kitchen HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Hospital Kitchen_Exhaust_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
Hospital Kitchen_Flr_5 sub cat Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital Kitchen_Flr_5 sub cat Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital Kitchen_Flr_5 sub cat Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital Kitchen_Flr_5 sub catHot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
Hospital Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital Kitchen_SAT_SCH | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
Hospital Lab_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital Lab_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital Lab_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital Lab_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital Lab_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital Lab_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital Lab_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital Lab_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital Labs_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital Labs_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital Laundry Setpoint Temp Schedule | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 82.22 | From DOE Prototype Buildings
Hospital LAUNDRY_SWH_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital MaxRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital MinRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 40 | From DOE Prototype Buildings
Hospital MinRelHumSetSch_addDI | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
Hospital MinRelHumSetSch_addDI_ICU | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 35 | From DOE Prototype Buildings
Hospital OR ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | From DOE Reference Buildings
Hospital OR HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 18.3 | From DOE Reference Buildings
Hospital OR_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital OR_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital OR_MinSA_Sched | Unknown |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital OR_MinSA_Sched | Unknown |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital OR_MinSA_Sched | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital OR_MinSA_Sched | Unknown |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital OR1_Flr_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital OR1_Flr_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital OR1_Flr_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital OR1_Flr_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital OR2_Mult5_Flr_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital OR2_Mult5_Flr_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital OR2_Mult5_Flr_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital OR2_Mult5_Flr_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital OR3_Flr_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital OR3_Flr_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital OR3_Flr_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital OR3_Flr_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital OR4_Flr_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital OR4_Flr_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital OR4_Flr_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital OR4_Flr_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital Patrms_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital Patrms_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital PatRoom1_Mult10_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PatRoom2_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PatRoom2_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PatRoom2_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PatRoom2_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PatRoom2_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PatRoom2_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PatRoom2_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PatRoom2_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PatRoom4_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PatRoom4_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PatRoom4_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PatRoom4_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PatRoom4_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PatRoom4_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PatRoom4_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PatRoom4_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PatRoom6_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PatRoom6_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PatRoom6_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PatRoom6_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PatRoom6_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PatRoom6_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PatRoom6_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PatRoom6_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PatRoom8_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PatRoom8_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PatRoom8_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PatRoom8_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PatRoom8_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PatRoom8_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PatRoom8_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PatRoom8_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PhysTherapy_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital PhysTherapy_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital PhysTherapy_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital PhysTherapy_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Hospital Radiology_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
Hospital Radiology_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
Hospital Radiology_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital Radiology_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
Hospital ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital scheduleOSCBasementFloorTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital scheduleOSCBasementLowerWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital scheduleOSCBasementUpperWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital scheduleOSCBasementWallSurfaceTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 22 | From DOE Prototype Buildings
Hospital SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Hospital Tower-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.1 | From DOE Prototype Buildings
Hospital VAV_ER_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.33 | From DOE Prototype Buildings
Hospital VAV_ICU_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.33 | From DOE Prototype Buildings
Hospital VAV_LABS_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital VAV_OR_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.33 | From DOE Prototype Buildings
Hospital VAV_PATRMS_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.33 | From DOE Prototype Buildings
Hospital VAV_SAT_SCH | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 12.8 | From DOE Prototype Buildings
Hospital walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital walkin_occ_lght_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.104 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Hospital walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.26 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.156 | 0.156 | 0.156 | 0.156 | 0.156 | 0.156 | 0.156 | 0.1 | From DOE Prototype Buildings
Hospital walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Hospital Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Hospital WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
HotelLarge Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.11 | From DOE Prototype Buildings
HotelLarge Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
HotelLarge Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.11 | From DOE Prototype Buildings
HotelLarge Adva5F_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
HotelLarge Adva5F_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.11 | From DOE Prototype Buildings
HotelLarge Adva5F_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
HotelLarge Adva5F_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.11 | From DOE Prototype Buildings
HotelLarge AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
HotelLarge ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge Base_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.11 | From DOE Prototype Buildings
HotelLarge Base_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.11 | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge BASEMENT_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH_2010 | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.38414 | 0.38414 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.38414 | 0.48018 | 0.48018 | 0.38414 | 0.38414 | 0.38414 | 0.38414 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.57621 | 0.76829 | 0.86432 | 0.67225 | 0.57621 | 0.38414 | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH_2010 | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.28811 | 0.28811 | 0.19207 | 0.19207 | 0.19207 | 0.19207 | 0.38414 | 0.38414 | 0.48018 | 0.48018 | 0.38414 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.67225 | 0.76829 | 0.76829 | 0.76829 | 0.67225 | 0.38414 | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH_2010 | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge BASEMENT_EQUIP_SCH_2010 | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.28811 | 0.24009 | 0.19207 | 0.19207 | 0.19207 | 0.28811 | 0.48018 | 0.57621 | 0.48018 | 0.48018 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.67225 | 0.86432 | 0.91234 | 0.86432 | 0.67225 | 0.38414 | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH_2010 | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
HotelLarge BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
HotelLarge BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
HotelLarge BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | From DOE Prototype Buildings
HotelLarge BLDG_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | From DOE Prototype Buildings
HotelLarge BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | From DOE Prototype Buildings
HotelLarge BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH_2010 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.25029 | 0.25029 | 0.16686 | 0.16686 | 0.16686 | 0.16686 | 0.25029 | 0.33372 | 0.33372 | 0.25029 | 0.25029 | 0.25029 | 0.25029 | 0.16686 | 0.16686 | 0.16686 | 0.16686 | 0.16686 | 0.41715 | 0.58401 | 0.66744 | 0.50058 | 0.41715 | 0.25029 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH_2010 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.16686 | 0.16686 | 0.08343 | 0.08343 | 0.08343 | 0.08343 | 0.25029 | 0.25029 | 0.33372 | 0.33372 | 0.25029 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.50058 | 0.58401 | 0.58401 | 0.58401 | 0.50058 | 0.25029 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH_2010 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge BLDG_LIGHT_CORRIDOR_SCH_2010 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.16686 | 0.12515 | 0.08343 | 0.08343 | 0.08343 | 0.16686 | 0.33372 | 0.41715 | 0.33372 | 0.33372 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.50058 | 0.66744 | 0.75087 | 0.66744 | 0.50058 | 0.25029 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH_2010 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge BLDG_LIGHT_GUESTROOM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2197 | 0.2197 | 0.0945 | 0.0945 | 0.0945 | 0.0945 | 0.3852 | 0.3852 | 0.5259 | 0.44427 | 0.30216 | 0.2432 | 0.2432 | 0.2432 | 0.2432 | 0.2432 | 0.2432 | 0.25327 | 0.7973 | 0.938 | 0.938 | 0.938 | 0.7973 | 0.3852 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1859 | 0.1452 | 0.0945 | 0.0945 | 0.0945 | 0.1859 | 0.4121 | 0.5259 | 0.4121 | 0.4121 | 0.2087 | 0.2087 | 0.2087 | 0.2087 | 0.2087 | 0.2087 | 0.21304 | 0.2149 | 0.6297 | 0.8342 | 0.938 | 0.8342 | 0.6297 | 0.3083 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH_2010 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.28125 | 0.28125 | 0.1875 | 0.1875 | 0.1875 | 0.1875 | 0.28125 | 0.375 | 0.375 | 0.28125 | 0.28125 | 0.28125 | 0.28125 | 0.1875 | 0.1875 | 0.1875 | 0.1875 | 0.1875 | 0.46875 | 0.65625 | 0.75 | 0.5625 | 0.46875 | 0.28125 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH_2010 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1875 | 0.1875 | 0.09375 | 0.09375 | 0.09375 | 0.09375 | 0.28125 | 0.28125 | 0.375 | 0.375 | 0.28125 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.5625 | 0.65625 | 0.65625 | 0.65625 | 0.5625 | 0.28125 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH_2010 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH_2010 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1875 | 0.14062 | 0.09375 | 0.09375 | 0.09375 | 0.1875 | 0.375 | 0.46875 | 0.375 | 0.375 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.5625 | 0.75 | 0.84375 | 0.75 | 0.5625 | 0.28125 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH_2010 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH_2010 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.17565 | 0.17565 | 0.1171 | 0.1171 | 0.1171 | 0.1171 | 0.17565 | 0.2342 | 0.2342 | 0.17565 | 0.17565 | 0.17565 | 0.17565 | 0.1171 | 0.1171 | 0.1171 | 0.1171 | 0.1171 | 0.29275 | 0.40985 | 0.4684 | 0.3513 | 0.29275 | 0.17565 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH_2010 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1171 | 0.1171 | 0.05855 | 0.05855 | 0.05855 | 0.05855 | 0.17565 | 0.17565 | 0.2342 | 0.2342 | 0.17565 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.3513 | 0.40985 | 0.40985 | 0.40985 | 0.3513 | 0.17565 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH_2010 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge BLDG_LIGHT_STORAGE_SCH_2010 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1171 | 0.087825 | 0.05855 | 0.05855 | 0.05855 | 0.1171 | 0.2342 | 0.29275 | 0.2342 | 0.2342 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.3513 | 0.4684 | 0.52695 | 0.4684 | 0.3513 | 0.17565 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH_2010 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | From DOE Prototype Buildings
HotelLarge BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | From DOE Prototype Buildings
HotelLarge BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | From DOE Prototype Buildings
HotelLarge BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | From DOE Prototype Buildings
HotelLarge BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | From DOE Prototype Buildings
HotelLarge BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | From DOE Prototype Buildings
HotelLarge Booster Water Inlet Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelLarge Booster Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 82.22 | From DOE Prototype Buildings
HotelLarge CLGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
HotelLarge CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
HotelLarge CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge Cool-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 12.8 | From DOE Prototype Buildings
HotelLarge CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 6.7 | From DOE Prototype Buildings
HotelLarge Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
HotelLarge ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Eqp_Sch | Equipment |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Eqp_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge EmployeeLounge_Eqp_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge EmployeeLounge_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge ExerciseRoom_Eqp_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | From DOE Prototype Buildings
HotelLarge ExerciseRoom_Occ_Sch | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | From DOE Prototype Buildings
HotelLarge Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge Exterior_Ltg_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
HotelLarge FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge FLR_3_DOAS_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge GuestRoom_Eqp_Sch_Adva | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.3 | 0.62 | 0.9 | 0.62 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.21 | 0.4 | 0.48 | 0.46 | 0.62 | 0.69 | 0.34 | 0.17 | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Adva | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge GuestRoom_Eqp_Sch_Adva | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.62 | 0.9 | 0.43 | 0.43 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.19 | 0.48 | 0.48 | 0.46 | 0.62 | 0.69 | 0.34 | 0.17 | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Adva | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Base | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Base | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge GuestRoom_Eqp_Sch_Base | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Base | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge GuestRoom_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
HotelLarge GuestRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge GuestRoom_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | From DOE Prototype Buildings
HotelLarge GuestRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge GuestRoom_SWH_Sch | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | From DOE Prototype Buildings
HotelLarge GuestRoom_SWH_Sch | Service Water Heating |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | From DOE Prototype Buildings
HotelLarge Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 16 | From DOE Prototype Buildings
HotelLarge Hours_of_operation | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge HTGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
HotelLarge Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 50 | From DOE Prototype Buildings
HotelLarge HVACOperationSchd | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelLarge INFIL_HALF_ON_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
HotelLarge INFIL_QUARTER_ON_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.25 | From DOE Prototype Buildings
HotelLarge INFIL_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | From DOE Prototype Buildings
HotelLarge Kitchen_Elec_Equip_SCH | Equipment |  | Default¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
HotelLarge Kitchen_Elec_Equip_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.3 | From DOE Prototype Buildings
HotelLarge Kitchen_Elec_Equip_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge Kitchen_Exhaust_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge Kitchen_Gas_Equip_SCH | Equipment |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | From DOE Prototype Buildings
HotelLarge Kitchen_Gas_Equip_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.25 | From DOE Prototype Buildings
HotelLarge Kitchen_Gas_Equip_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge Laundry Setpoint Temp Schedule | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 82.22 | From DOE Prototype Buildings
HotelLarge LAUNDRY_SWH_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
HotelLarge LaundryRoom_Eqp_Elec_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge LaundryRoom_Eqp_Elec_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge LaundryRoom_Eqp_Elec_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge LaundryRoom_Eqp_Gas_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge LaundryRoom_Eqp_Gas_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge LaundryRoom_Eqp_Gas_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge LaundryRoom_Occ_Sch | Occupancy |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge LaundryRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge LaundryRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge LaundryRoom_SWH_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge Lobby_Eqp_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21 | From DOE Prototype Buildings
HotelLarge Lobby_Eqp_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge Lobby_Eqp_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge Lobby_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Prototype Buildings
HotelLarge Lobby_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge Lobby_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Prototype Buildings
HotelLarge Lobby_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge MaxRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelLarge MeetingRoom_Eqp_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge MeetingRoom_Occ_Sch | Occupancy |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge MeetingRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge MeetingRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge MinOA_MotorizedDamper_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge MinRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
HotelLarge N Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelLarge N Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.111 | From DOE Prototype Buildings
HotelLarge N Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelLarge N Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.111 | From DOE Prototype Buildings
HotelLarge Off During Unoccupied Period | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge Office_Eqp_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Prototype Buildings
HotelLarge Office_Eqp_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge Office_Eqp_Sch | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Prototype Buildings
HotelLarge Office_Eqp_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge Office_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
HotelLarge Office_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge Office_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
HotelLarge Office_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelLarge ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge Room_1_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
HotelLarge Room_1_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
HotelLarge Room_1_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
HotelLarge Room_1_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelLarge Room_1_Flr_6 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
HotelLarge Room_1_Flr_6 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
HotelLarge Room_1_Flr_6 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
HotelLarge Room_1_Flr_6 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelLarge Room_2_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
HotelLarge Room_2_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
HotelLarge Room_2_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
HotelLarge Room_2_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelLarge Room_2_Flr_6 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
HotelLarge Room_2_Flr_6 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
HotelLarge Room_2_Flr_6 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
HotelLarge Room_2_Flr_6 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelLarge Room_3_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
HotelLarge Room_3_Mult19_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
HotelLarge Room_3_Mult19_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
HotelLarge Room_3_Mult19_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelLarge Room_3_Mult9_Flr_6 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
HotelLarge Room_3_Mult9_Flr_6 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
HotelLarge Room_3_Mult9_Flr_6 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
HotelLarge Room_3_Mult9_Flr_6 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelLarge Room_4_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
HotelLarge Room_4_Mult19_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
HotelLarge Room_4_Mult19_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
HotelLarge Room_4_Mult19_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelLarge Room_5_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
HotelLarge Room_5_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
HotelLarge Room_5_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
HotelLarge Room_5_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelLarge Room_6_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
HotelLarge Room_6_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
HotelLarge Room_6_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
HotelLarge Room_6_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelLarge S Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelLarge S Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.111 | From DOE Prototype Buildings
HotelLarge S Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelLarge S Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.111 | From DOE Prototype Buildings
HotelLarge scheduleOSCBasementFloorTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge scheduleOSCBasementLowerWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge scheduleOSCBasementUpperWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge scheduleOSCBasementWallSurfaceTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
HotelLarge Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
HotelLarge Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
HotelLarge SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
HotelLarge Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge SWHSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 22 | From DOE Prototype Buildings
HotelLarge SWHSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelLarge SWHSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelLarge walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.156 | 0.156 | 0.104 | 0.104 | 0.104 | 0.104 | 0.156 | 0.208 | 0.208 | 0.156 | 0.156 | 0.156 | 0.156 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.26 | 0.364 | 0.416 | 0.312 | 0.26 | 0.156 | From DOE Prototype Buildings
HotelLarge walkin_occ_lght_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.104 | 0.104 | 0.052 | 0.052 | 0.052 | 0.052 | 0.156 | 0.156 | 0.208 | 0.208 | 0.156 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.312 | 0.364 | 0.364 | 0.364 | 0.312 | 0.156 | From DOE Prototype Buildings
HotelLarge walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelLarge walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.104 | 0.078 | 0.052 | 0.052 | 0.052 | 0.104 | 0.208 | 0.26 | 0.208 | 0.208 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.312 | 0.416 | 0.468 | 0.416 | 0.312 | 0.156 | From DOE Prototype Buildings
HotelLarge walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelLarge WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall Adva_EmployeeLounge_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 26.667 | 26.667 | 26.667 | 26.667 | From DOE Prototype Buildings
HotelSmall Adva_EmployeeLounge_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.333 | 18.333 | 18.333 | 18.333 | From DOE Prototype Buildings
HotelSmall Adva_ExerciseCenter_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 26.667 | From DOE Prototype Buildings
HotelSmall Adva_ExerciseCenter_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.333 | From DOE Prototype Buildings
HotelSmall Adva_MeetingRoom_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | From DOE Prototype Buildings
HotelSmall Adva_MeetingRoom_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | From DOE Prototype Buildings
HotelSmall Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.111 | From DOE Prototype Buildings
HotelSmall Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.111 | From DOE Prototype Buildings
HotelSmall Adva5F_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall Adva5F_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.111 | From DOE Prototype Buildings
HotelSmall Adva5F_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall Adva5F_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.111 | From DOE Prototype Buildings
HotelSmall AlwaysOff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall AlwaysOff_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall AlwaysOn | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelSmall AlwaysOn_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall Base_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.111 | From DOE Prototype Buildings
HotelSmall Base_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.111 | From DOE Prototype Buildings
HotelSmall BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
HotelSmall BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
HotelSmall BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall BLDG_LIGHT_CORRIDOR_SCH_2013 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.65 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_EXERCENTER_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2010 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2197 | 0.2197 | 0.0945 | 0.0945 | 0.0945 | 0.0945 | 0.3852 | 0.3852 | 0.5259 | 0.44427 | 0.30216 | 0.2432 | 0.2432 | 0.2432 | 0.2432 | 0.2432 | 0.2432 | 0.25327 | 0.7973 | 0.939 | 0.939 | 0.939 | 0.7973 | 0.3852 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2010 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2010 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1859 | 0.1452 | 0.0945 | 0.0945 | 0.0945 | 0.1859 | 0.4121 | 0.5259 | 0.4121 | 0.4121 | 0.2087 | 0.2087 | 0.2087 | 0.2087 | 0.2087 | 0.2087 | 0.21304 | 0.2149 | 0.6297 | 0.8342 | 0.938 | 0.8342 | 0.6297 | 0.3083 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2010 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2013 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.13 | 0.13 | 0.06 | 0.06 | 0.06 | 0.06 | 0.33 | 0.33 | 0.45 | 0.18667 | 0.062121 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0825 | 0.68 | 0.8 | 0.8 | 0.8 | 0.68 | 0.33 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2013 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2013 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.09 | 0.06 | 0.06 | 0.06 | 0.11 | 0.35 | 0.45 | 0.45 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.05 | 0.064 | 0.07 | 0.54 | 0.71 | 0.8 | 0.71 | 0.54 | 0.26 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2013 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_LAUNDRY_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_MECHROOM_SCH | Lighting |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_MECHROOM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelSmall BLDG_LIGHT_MECHROOM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.50935 | 0.7515 | 0.7515 | 0.7515 | 0.7515 | 0.668 | 0.7515 | 0.7515 | 0.7515 | 0.7515 | 0.50935 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelSmall BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_RESTROOM_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.66 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_STAIR_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.55 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_STORAGE_SCH | Lighting |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05418 | 0.05418 | 0.05418 | 0.05418 | 0.05418 | 0.05418 | 0.05418 | 0.10836 | 0.21672 | 0.21672 | 0.21672 | 0.21672 | 0.21672 | 0.21672 | 0.21672 | 0.21672 | 0.21672 | 0.21672 | 0.10836 | 0.10836 | 0.10836 | 0.10836 | 0.05418 | 0.05418 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_STORAGE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall BLDG_LIGHT_STORAGE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall CommonArea_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 23.889 | From DOE Prototype Buildings
HotelSmall CommonArea_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.111 | From DOE Prototype Buildings
HotelSmall CommonArea_Infil_Sch | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.25 | From DOE Prototype Buildings
HotelSmall CommonArea_Infil_Sch | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelSmall CommonArea_Infil_Sch | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall COMPACT HVAC-ALWAYS 0 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall COMPACT HVAC-ALWAYS 1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelSmall COMPACT HVAC-ALWAYS 4 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
HotelSmall ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelSmall ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
HotelSmall ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
HotelSmall ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Eqp_Sch | Equipment |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Eqp_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelSmall EmployeeLounge_Eqp_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall EmployeeLounge_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall ExerciseCenter_Eqp_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | From DOE Prototype Buildings
HotelSmall ExerciseCenter_Occ_Sch | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | From DOE Prototype Buildings
HotelSmall Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall Exterior_Ltg_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Adva | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.3 | 0.62 | 0.9 | 0.62 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.21 | 0.4 | 0.48 | 0.46 | 0.62 | 0.69 | 0.34 | 0.09 | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Adva | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall GuestRoom_Eqp_Sch_Adva | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.62 | 0.9 | 0.43 | 0.43 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.19 | 0.48 | 0.48 | 0.46 | 0.62 | 0.69 | 0.34 | 0.09 | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Adva | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Base | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Base | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall GuestRoom_Eqp_Sch_Base | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Base | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall GuestRoom_Infil_Sch | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.25 | From DOE Prototype Buildings
HotelSmall GuestRoom_Infil_Sch | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall GuestRoom_Infil_Sch | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall GuestRoom_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77 | From DOE Prototype Buildings
HotelSmall GuestRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelSmall GuestRoom_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1 | From DOE Prototype Buildings
HotelSmall GuestRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall GuestRoom_SHW_Sch | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | From DOE Prototype Buildings
HotelSmall GuestRoom_SHW_Sch | Service Water Heating |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | From DOE Prototype Buildings
HotelSmall Heat Exchanger Supply Air Temp Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 14 | From DOE Prototype Buildings
HotelSmall INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0 | From DOE Prototype Buildings
HotelSmall LaundryRoom_Eqp_Elec_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall LaundryRoom_Eqp_Elec_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelSmall LaundryRoom_Eqp_Elec_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall LaundryRoom_Eqp_Gas_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall LaundryRoom_Eqp_Gas_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall LaundryRoom_Eqp_Gas_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall LaundryRoom_Occ_Sch | Occupancy |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall LaundryRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelSmall LaundryRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall LaundryRoom_SHW_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall Lobby_Eqp_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21 | From DOE Prototype Buildings
HotelSmall Lobby_Eqp_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelSmall Lobby_Eqp_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall Lobby_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Prototype Buildings
HotelSmall Lobby_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall Lobby_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Prototype Buildings
HotelSmall Lobby_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall MeetingRoom_Eqp_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall MeetingRoom_Occ_Sch | Occupancy |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall MeetingRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
HotelSmall MeetingRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall MinOA_MotorizedDamper_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall N Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall N Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.111 | From DOE Prototype Buildings
HotelSmall N Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall N Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.111 | From DOE Prototype Buildings
HotelSmall Off During Unoccupied Period | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall OFF_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Prototype Buildings
HotelSmall OFF_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall OFF_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Prototype Buildings
HotelSmall OFF_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall Office_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
HotelSmall Office_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall Office_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
HotelSmall Office_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
HotelSmall S Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall S Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.111 | From DOE Prototype Buildings
HotelSmall S Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall S Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.111 | From DOE Prototype Buildings
HotelSmall SAC_Econ_MaxOAFrac_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.7
HotelSmall SemiHeated_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 7.2 | From DOE Prototype Buildings
HotelSmall SHW Latent fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
HotelSmall SHW Laundry Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 82.22 | From DOE Prototype Buildings
HotelSmall SHW Sensible fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
HotelSmall SHW Shower Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelSmall SHWSys Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.1 | From DOE Prototype Buildings
HotelSmall SHWSysLaundry Water Heater Setpoint Temperature Schedule | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelSmall SHWSysLaundry-Loop-Temp-Schedule | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelSmall SHWSysShower Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelSmall SHWSysShower-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
HotelSmall Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
HotelSmall Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
HotelSmall VacGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 23.333 | From DOE Prototype Buildings
HotelSmall VacGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 18.889 | From DOE Prototype Buildings
Large Office BLDG ELEVATORS | Elevator |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Reference Buildings
Large Office Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | From DOE Reference Buildings
Large Office Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Large Office Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Large Office Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.3 | From DOE Reference Buildings
Large Office Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Large Office Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | From DOE Reference Buildings
Large Office Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Large Office Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Large Office Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Reference Buildings
Large Office Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Large Office Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
Large Office Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Large Office Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Reference Buildings
Large Office Bldg Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Large Office ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Reference Buildings
Large Office ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Reference Buildings
Large Office ClgSetp | Thermostat Setpoint | C | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Reference Buildings
Large Office Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Large Office Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
Large Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Large Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
Large Office HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
Large Office HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Large Office HtgSetp | Thermostat Setpoint | C | SmrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Reference Buildings
Large Office HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Reference Buildings
Large Office Infil Quarter On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Reference Buildings
Large Office Infil Quarter On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Large Office Infil Quarter On | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
Large Office Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
LargeHotel BLDG ELEVATORS | Elevator |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Reference Buildings
LargeHotel Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | From DOE Reference Buildings
LargeHotel Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | From DOE Reference Buildings
LargeHotel Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
LargeHotel Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | From DOE Reference Buildings
LargeHotel Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
LargeHotel Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Reference Buildings
LargeHotel Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Reference Buildings
LargeHotel Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
LargeHotel Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Reference Buildings
LargeHotel Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
LargeHotel Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | From DOE Reference Buildings
LargeHotel Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | From DOE Reference Buildings
LargeHotel Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
LargeHotel Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | From DOE Reference Buildings
LargeHotel Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
LargeHotel ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Reference Buildings
LargeHotel Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
LargeHotel Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
LargeHotel Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
LargeHotel Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
LargeHotel Common Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
LargeHotel Common Occ | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Reference Buildings
LargeHotel Common Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Reference Buildings
LargeHotel Common Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0
LargeHotel Corridor ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Reference Buildings
LargeHotel Corridor HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 16 | From DOE Reference Buildings
LargeHotel GuestRoom ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Reference Buildings
LargeHotel GuestRoom Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Reference Buildings
LargeHotel GuestRoom Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
LargeHotel GuestRoom Equip | Equipment |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Reference Buildings
LargeHotel GuestRoom Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
LargeHotel GuestRoom HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Reference Buildings
LargeHotel GuestRoom Occ | Occupancy |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | From DOE Reference Buildings
LargeHotel GuestRoom Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
LargeHotel GuestRoom Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
LargeHotel GuestRoom Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
LargeHotel GuestRoom_Ltg_Sch_Base | Lighting |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
LargeHotel GuestRoom_Ltg_Sch_Base | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | From DOE Reference Buildings
LargeHotel GuestRoom_Ltg_Sch_Base | Lighting |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | From DOE Reference Buildings
LargeHotel GuestRoom_Ltg_Sch_Base | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
LargeHotel HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | From DOE Reference Buildings
LargeHotel Infil Quarter On | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.25 | From DOE Reference Buildings
LargeHotel Kitchen ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Reference Buildings
LargeHotel Kitchen Equip | Equipment |  | Default¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
LargeHotel Kitchen Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.35 | From DOE Reference Buildings
LargeHotel Kitchen Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
LargeHotel Kitchen Exhaust | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
LargeHotel Kitchen Gas | Equipment |  | Default¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | From DOE Reference Buildings
LargeHotel Kitchen Gas | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.25 | From DOE Reference Buildings
LargeHotel Kitchen Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
LargeHotel Kitchen HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | From DOE Reference Buildings
LargeHotel Kitchen_Elec_Equip_SCH | Equipment |  | Default¦Wkdy¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
LargeHotel Kitchen_Elec_Equip_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.35 | From DOE Reference Buildings
LargeHotel Kitchen_Elec_Equip_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
LargeHotel LaundryRoom Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
LargeHotel LaundryRoom Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
LargeHotel LaundryRoom Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
LargeHotel LaundryRoom Gas | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
LargeHotel LaundryRoom Gas | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
LargeHotel LaundryRoom Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
LargeHotel Lobby Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Reference Buildings
LargeHotel Lobby Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
LargeHotel Lobby Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Reference Buildings
LargeHotel Lobby Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
LargeHotel Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Medium Office BLDG ELEVATORS | Elevator |  | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Medium Office BLDG ELEVATORS | Elevator |  | Wkdy¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | From DOE Reference Buildings
Medium Office BLDG ELEVATORS | Elevator |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Medium Office Bldg Equip | Equipment |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | From DOE Reference Buildings
Medium Office Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Medium Office Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Medium Office Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.3 | From DOE Reference Buildings
Medium Office Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Medium Office Bldg Light | Lighting |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Medium Office Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Reference Buildings
Medium Office Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Medium Office Bldg Occ | Occupancy |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Medium Office Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Medium Office Bldg Swh | Service Water Heating |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Swh | Service Water Heating |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | From DOE Reference Buildings
Medium Office Bldg Swh | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | From DOE Reference Buildings
Medium Office ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Reference Buildings
Medium Office ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Reference Buildings
Medium Office ClgSetp | Thermostat Setpoint | C | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Reference Buildings
Medium Office Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Medium Office Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
Medium Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Medium Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
Medium Office HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
Medium Office HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Medium Office HtgSetp | Thermostat Setpoint | C | SmrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Reference Buildings
Medium Office HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Reference Buildings
Medium Office Infil Quarter On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Reference Buildings
Medium Office Infil Quarter On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Medium Office Infil Quarter On | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
Medium Office Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
MidriseApartment Apartment ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 23.9 | From DOE Reference Buildings
MidriseApartment Apartment DHW | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29 | From DOE Reference Buildings
MidriseApartment Apartment Equip | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58 | From DOE Reference Buildings
MidriseApartment Apartment HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.1 | From DOE Reference Buildings
MidriseApartment Apartment Light | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.067 | 0.067 | 0.067 | 0.067 | 0.187 | 0.394 | 0.44 | 0.393 | 0.172 | 0.119 | 0.119 | 0.119 | 0.119 | 0.119 | 0.119 | 0.206 | 0.439 | 0.616 | 0.829 | 0.986 | 1 | 0.692 | 0.384 | 0.16 | From DOE Reference Buildings
MidriseApartment Apartment Occ | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1 | From DOE Reference Buildings
MidriseApartment Apartment Operation | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
MidriseApartment BLDG ELEVATORS | Elevator |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Reference Buildings
MidriseApartment Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
MidriseApartment Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
MidriseApartment Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
MidriseApartment Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
MidriseApartment Corridor ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 40 | From DOE Reference Buildings
MidriseApartment Corridor HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Reference Buildings
MidriseApartment Corridor Light | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
MidriseApartment Infil | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
MidriseApartment Office ClgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Reference Buildings
MidriseApartment Office ClgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Reference Buildings
MidriseApartment Office ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.4 | From DOE Reference Buildings
MidriseApartment Office Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | From DOE Reference Buildings
MidriseApartment Office Equip | Equipment |  | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.33 | From DOE Reference Buildings
MidriseApartment Office HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
MidriseApartment Office HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Reference Buildings
MidriseApartment Office HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
MidriseApartment OFFICE Infil | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
MidriseApartment OFFICE Infil | Infiltration |  | WntrDsn¦SmrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
MidriseApartment Office Light | Lighting |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | From DOE Reference Buildings
MidriseApartment Office Light | Lighting |  | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.18 | From DOE Reference Buildings
MidriseApartment Office Occ | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
MidriseApartment Office Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
MidriseApartment Office Operation | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
MidriseApartment Office Operation | Operation |  | Wknd | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
MidriseApartment UnitHeater ClgSP Sch | Thermostat Setpoint |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
MidriseApartment UnitHeater HtgSP Sch | Thermostat Setpoint |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
MidriseApartment Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
NECB-A-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2
NECB-A-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
NECB-A-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
NECB-A-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
NECB-A-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-A-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-A-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.5 | 0.3 | 0.3 | 0.1 | 0.1 | 0.05
NECB-A-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-A-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-A-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.7 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.7 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0
NECB-A-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-A-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-A-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2
NECB-A-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
NECB-A-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
NECB-A-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05
NECB-A-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-A-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-A-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35 | 35 | 35
NECB-A-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
NECB-A-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
NECB-A-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18
NECB-A-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NECB-A-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NECB-B-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-B-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-B-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5
NECB-B-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-B-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-B-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
NECB-B-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-B-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-B-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5
NECB-B-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.9 | 0.8 | 0.5 | 0.2 | 0.2 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.6 | 0.4
NECB-B-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.9 | 0.8 | 0.5 | 0.2 | 0.2 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6
NECB-B-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.4 | 0.5 | 0.5 | 0.4 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.7 | 0.5 | 0.3 | 0.1
NECB-B-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-B-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-B-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5
NECB-B-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.6 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 0.7 | 0.4 | 0.5 | 0.6 | 0.6 | 0.4 | 0.3 | 0.3 | 0.4 | 0.5 | 0.8 | 0.8 | 0.9 | 0.9
NECB-B-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.6 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 0.7 | 0.4 | 0.5 | 0.6 | 0.6 | 0.4 | 0.3 | 0.3 | 0.4 | 0.5 | 0.8 | 0.8 | 0.9 | 0.9
NECB-B-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.6 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 0.7 | 0.4 | 0.5 | 0.6 | 0.6 | 0.4 | 0.3 | 0.3 | 0.4 | 0.5 | 0.8 | 0.8 | 0.5 | 0.5
NECB-B-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-B-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-B-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35
NECB-B-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-B-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-B-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 18 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18
NECB-C-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.5 | 0.05 | 0.05 | 0.05
NECB-C-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.5 | 0.05 | 0.05 | 0.05
NECB-C-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-C-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
NECB-C-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
NECB-C-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
NECB-C-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.5 | 0.05 | 0.05 | 0.05
NECB-C-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.5 | 0.05 | 0.05 | 0.05
NECB-C-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-C-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
NECB-C-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.7 | 0.5 | 0.2 | 0.2 | 0 | 0 | 0
NECB-C-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0 | 0 | 0 | 0 | 0
NECB-C-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.5 | 0.05 | 0.05 | 0.05
NECB-C-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.5 | 0.05 | 0.05 | 0.05
NECB-C-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-C-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.3 | 0.4 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.3 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05
NECB-C-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.3 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05
NECB-C-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.8 | 0.8 | 0.6 | 0.4 | 0.3 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-C-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35 | 35 | 35
NECB-C-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35 | 35 | 35
NECB-C-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35 | 35 | 35 | 35 | 35
NECB-C-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18
NECB-C-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18
NECB-C-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | 18
NECB-D-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.3 | 0.05
NECB-D-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-D-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-D-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
NECB-D-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-D-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-D-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.3 | 0.05
NECB-D-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-D-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-D-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.2 | 0.1 | 0.3 | 0.3 | 0.3 | 0.1 | 0
NECB-D-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-D-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-D-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.3 | 0.05
NECB-D-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-D-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-D-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.3 | 0.5 | 0.5 | 0.5 | 0.3 | 0.05 | 0.05
NECB-D-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-D-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-D-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35
NECB-D-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
NECB-D-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
NECB-D-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18
NECB-D-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NECB-D-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NECB-E-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
NECB-E-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-E-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-E-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.9 | 0.8 | 0.8 | 0.2 | 0 | 0 | 0 | 0 | 0
NECB-E-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-E-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-E-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.5 | 0.5 | 0.7 | 0.9 | 0.8 | 0.7 | 0.8 | 0.3 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.4 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35 | 35 | 35 | 35 | 35
NECB-E-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35
NECB-E-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
NECB-E-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | 18
NECB-E-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NECB-E-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NECB-F-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6
NECB-F-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6
NECB-F-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5
NECB-F-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | bar: Hr 1 to Hr 24
NECB-F-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | bar: Hr 1 to Hr 24
NECB-F-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | bar: Hr 1 to Hr 24
NECB-F-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6
NECB-F-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6
NECB-F-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5
NECB-F-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9
NECB-F-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7
NECB-F-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8
NECB-F-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6
NECB-F-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6
NECB-F-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5
NECB-F-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.3 | 0.2 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.9 | 0.7 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7
NECB-F-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.3 | 0.2 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.8 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.3 | 0.3 | 0.3 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7
NECB-F-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.3 | 0.2 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.6 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6
NECB-F-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-F-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-F-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-F-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-F-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-F-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-G-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.2 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5
NECB-G-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.2 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5
NECB-G-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.2 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5
NECB-G-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | bar: Hr 1 to Hr 24
NECB-G-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | bar: Hr 1 to Hr 24
NECB-G-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | bar: Hr 1 to Hr 24
NECB-G-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6
NECB-G-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6
NECB-G-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6
NECB-G-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-G-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-G-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-G-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.2 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5
NECB-G-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.2 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5
NECB-G-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.2 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5
NECB-G-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.8 | 0.7 | 0.5 | 0.4 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.1
NECB-G-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.7 | 0.6 | 0.5 | 0.4 | 0.3 | 0.2
NECB-G-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.3 | 0.3 | 0.2 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2
NECB-G-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-G-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-G-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-G-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-G-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-G-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-H-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | bar: Hr 1 to Hr 24
NECB-H-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | bar: Hr 1 to Hr 24
NECB-H-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | bar: Hr 1 to Hr 24
NECB-H-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-H-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-H-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-H-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-H-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-H-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-I-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
NECB-I-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
NECB-I-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
NECB-I-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-I-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-I-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-I-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.5 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-I-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.5 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9
NECB-I-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-I-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.4 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4
NECB-I-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.4 | 0.6 | 0.8 | 0.6 | 0.4 | 0.2 | 0.4 | 0.8 | 0.8 | 0.6 | 0.4
NECB-I-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.4 | 0.8 | 0.8 | 0.4 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-I-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
NECB-I-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
NECB-I-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
NECB-I-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6
NECB-I-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.2 | 0.4 | 0.8 | 0.9 | 0.8 | 0.6 | 0.4 | 0.4 | 0.9 | 0.9 | 0.8 | 0.6
NECB-I-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.4 | 0.2 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-I-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-I-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-I-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
NECB-I-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-I-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-I-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Office Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | From DOE Reference Buildings
Office Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Office Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Office Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.3 | From DOE Reference Buildings
Office Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Office Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | From DOE Reference Buildings
Office Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Office Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Office Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Reference Buildings
Office Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Office Infil Quarter On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Reference Buildings
Office Infil Quarter On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Office Infil Quarter On | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
Office Misc Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
Office Misc Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Office Misc Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Reference Buildings
Office Misc Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Office Work Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.85 | 0.85 | 0.85 | 0.85 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
Office Work Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Office Work Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Reference Buildings
Office Work Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
OfficeLarge AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeLarge ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeLarge ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeLarge BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
OfficeLarge BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
OfficeLarge BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.3 | From DOE Prototype Buildings
OfficeLarge BLDG_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OfficeLarge BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeLarge BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
OfficeLarge BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeLarge BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeLarge BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeLarge BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeLarge BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | From DOE Prototype Buildings
OfficeLarge BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeLarge CLGSETP_DC_SCH | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeLarge CLGSETP_DC_SCH | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 27 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_CAV_bas | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦WntrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
OfficeLarge CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeLarge CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeLarge CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeLarge CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeLarge Cool-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 12.8 | From DOE Prototype Buildings
OfficeLarge Core_bottom sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeLarge Core_bottom sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeLarge Core_bottom sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeLarge Core_bottom sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeLarge Core_mid sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeLarge Core_mid sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeLarge Core_mid sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeLarge Core_mid sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeLarge Core_top sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeLarge Core_top sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeLarge Core_top sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeLarge Core_top sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeLarge CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 6.7 | From DOE Prototype Buildings
OfficeLarge DataCenter_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeLarge DataCenter_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeLarge DC_MinRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
OfficeLarge Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
OfficeLarge ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeLarge Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
OfficeLarge Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeLarge EXTERIOR_LIGHT_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | From DOE Prototype Buildings
OfficeLarge FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeLarge Heat-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 12.8 | From DOE Prototype Buildings
OfficeLarge Hours_of_operation | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeLarge Hours_of_operation | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge Hours_of_operation | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge HTGSETP_DC_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_CAV_bas | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HVACOperationSchd | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeLarge HVACOperationSchd | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge HVACOperationSchd | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 82 | From DOE Prototype Buildings
OfficeLarge INFIL_HALF_ON_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeLarge INFIL_HALF_ON_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge INFIL_HALF_ON_SCH | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeLarge INFIL_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge INFIL_SCH | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge INFIL_SCH_PNNL | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeLarge INFIL_SCH_PNNL | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge INFIL_SCH_PNNL | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeLarge MinOA_MotorizedDamper_Sched | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeLarge PLANT LOOP HIGH TEMP SCHEDULE | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 18.33 | From DOE Prototype Buildings
OfficeLarge PLANT LOOP LOW TEMP SCHEDULE | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 5 | From DOE Prototype Buildings
OfficeLarge PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeLarge ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeLarge scheduleOSCBasementFloorTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeLarge scheduleOSCBasementLowerWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeLarge scheduleOSCBasementUpperWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeLarge scheduleOSCBasementWallSurfaceTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeLarge SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeLarge SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 22 | From DOE Prototype Buildings
OfficeLarge SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeLarge SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeLarge SupplyFanSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeLarge Tower-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.1 | From DOE Prototype Buildings
OfficeLarge WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeMedium AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeMedium ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeMedium ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeMedium BLDG_ELEVATORS | Elevator |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.69 | From DOE Prototype Buildings
OfficeMedium BLDG_ELEVATORS | Elevator |  | Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeMedium BLDG_ELEVATORS | Elevator |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2004 | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2004 | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeMedium BLDG_EQUIP_SCH_2004 | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.3 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2004 | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2004 | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2010 | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.38414 | 0.38414 | 0.48018 | 0.48018 | 0.48018 | 0.48018 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.28811 | 0.28811 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2010 | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeMedium BLDG_EQUIP_SCH_2010 | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2010 | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.38414 | 0.38414 | 0.86432 | 0.86432 | 0.86432 | 0.86432 | 0.76829 | 0.86432 | 0.86432 | 0.86432 | 0.86432 | 0.48018 | 0.38414 | 0.38414 | 0.38414 | 0.38414 | 0.38414 | 0.38414 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2010 | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2013 | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.23076 | 0.23076 | 0.23076 | 0.23076 | 0.23076 | 0.23076 | 0.38123 | 0.38123 | 0.47654 | 0.47654 | 0.47654 | 0.47654 | 0.33358 | 0.33358 | 0.33358 | 0.33358 | 0.33358 | 0.28593 | 0.28593 | 0.23076 | 0.23076 | 0.23076 | 0.23076 | 0.23076 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2013 | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeMedium BLDG_EQUIP_SCH_2013 | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.23076 | 0.23076 | 0.23076 | 0.23076 | 0.23076 | 0.23076 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2013 | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.30767 | 0.30767 | 0.30767 | 0.30767 | 0.30767 | 0.30767 | 0.38123 | 0.38123 | 0.85778 | 0.85778 | 0.85778 | 0.85778 | 0.76247 | 0.85778 | 0.85778 | 0.85778 | 0.85778 | 0.47654 | 0.38123 | 0.38123 | 0.38123 | 0.38123 | 0.38123 | 0.38123 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2013 | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2004 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2004 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeMedium BLDG_LIGHT_SCH_2004 | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2004 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2004 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2010 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0904 | 0.0904 | 0.2712 | 0.2712 | 0.2712 | 0.2712 | 0.1356 | 0.1356 | 0.1356 | 0.1356 | 0.1356 | 0.0452 | 0.0452 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2010 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeMedium BLDG_LIGHT_SCH_2010 | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2010 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.0904 | 0.2712 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.452 | 0.2712 | 0.2712 | 0.1808 | 0.1808 | 0.0904 | 0.0452 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2010 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2013 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.086233 | 0.086233 | 0.2587 | 0.2587 | 0.2587 | 0.2587 | 0.12935 | 0.12935 | 0.12935 | 0.12935 | 0.12935 | 0.043116 | 0.043116 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2013 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeMedium BLDG_LIGHT_SCH_2013 | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2013 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.086233 | 0.2587 | 0.77609 | 0.77609 | 0.77609 | 0.77609 | 0.77609 | 0.77609 | 0.77609 | 0.77609 | 0.77609 | 0.43116 | 0.2587 | 0.2587 | 0.17247 | 0.17247 | 0.086233 | 0.043116 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2013 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeMedium BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeMedium BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦WntrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
OfficeMedium CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeMedium CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeMedium CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeMedium CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeMedium Cool-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 12.8 | From DOE Prototype Buildings
OfficeMedium Core_bottom sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeMedium Core_bottom sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeMedium Core_bottom sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium Core_bottom sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeMedium Core_mid sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeMedium Core_mid sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeMedium Core_mid sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium Core_mid sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeMedium Core_top sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeMedium Core_top sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeMedium Core_top sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium Core_top sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeMedium CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 6.7 | From DOE Prototype Buildings
OfficeMedium Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
OfficeMedium ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.69 | From DOE Prototype Buildings
OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium Exterior_Lgt_189_1 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
OfficeMedium Exterior_Lgt_ALWAYS_ON | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeMedium Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeMedium Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeMedium FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeMedium Heat-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 12.8 | From DOE Prototype Buildings
OfficeMedium Hours_of_operation | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeMedium Hours_of_operation | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium Hours_of_operation | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 50 | From DOE Prototype Buildings
OfficeMedium HVACOperationSchd | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeMedium HVACOperationSchd | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium HVACOperationSchd | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeMedium INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium INFIL_SCH_PNNL | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeMedium INFIL_SCH_PNNL | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Prototype Buildings
OfficeMedium INFIL_SCH_PNNL | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeMedium MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeMedium MinOA_MotorizedDamper_Sched | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeMedium Perimeter_bot_ZN_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeMedium PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeMedium ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeMedium SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeMedium SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 22 | From DOE Prototype Buildings
OfficeMedium SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeMedium VAV OA Damper | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0%
OfficeMedium VAV OA Damper | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | bar: Hr 1 to Hr 24
OfficeMedium VAV Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0%
OfficeMedium VAV Operation | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | bar: Hr 1 to Hr 24
OfficeMedium WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeSmall AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeSmall ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeSmall ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeSmall BLDG_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeSmall BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeSmall BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
OfficeSmall BLDG_LIGHT_SCH | Lighting |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeSmall BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeSmall BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.23 | 0.42 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.42 | 0.42 | 0.32 | 0.32 | 0.23 | 0.18 | From DOE Prototype Buildings
OfficeSmall BLDG_OCC_SCH | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeSmall BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeSmall BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.53 | 1 | 1 | 1 | 1 | 0.32 | 0.11 | 0.11 | 0.11 | 0.11 | 0.05 | 0 | From DOE Prototype Buildings
OfficeSmall BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeSmall BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 0.55 | 0.64 | 0.64 | 0.82 | 1 | 0.91 | 0.55 | 0.55 | 0.73 | 0.37 | 0.37 | 0.18 | 0.27 | 0.09 | 0 | 0 | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 23.89 | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 23.89 | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 23.89 | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 23.89 | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 23.89 | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
OfficeSmall CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
OfficeSmall CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeSmall CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeSmall CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeSmall CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeSmall Core_ZN Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OfficeSmall Core_ZN Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OfficeSmall Core_ZN Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OfficeSmall Core_ZN Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 48.8 | From DOE Prototype Buildings
OfficeSmall CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 6.7 | From DOE Prototype Buildings
OfficeSmall Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
OfficeSmall Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
OfficeSmall Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeSmall Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeSmall Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeSmall Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 16 | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.11 | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21.11 | From DOE Prototype Buildings
OfficeSmall Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 50 | From DOE Prototype Buildings
OfficeSmall HVACOperationSchd | Operation |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeSmall HVACOperationSchd | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeSmall HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeSmall INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeSmall INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeSmall INFIL_QUARTER_ON_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeSmall INFIL_QUARTER_ON_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeSmall INFIL_QUARTER_ON_SCH | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeSmall MinOA_MotorizedDamper_Sched | OA Air |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeSmall MinOA_MotorizedDamper_Sched | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeSmall MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeSmall PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OfficeSmall ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OfficeSmall Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
OfficeSmall Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
OfficeSmall Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
OfficeSmall SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OfficeSmall SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 22 | From DOE Prototype Buildings
OfficeSmall SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeSmall SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OfficeSmall WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Outpatient BLDG ELEVATORS | Elevator |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient BLDG ELEVATORS | Elevator |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient BLDG ELEVATORS | Elevator |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient Bldg Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Outpatient Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Outpatient Bldg Equip | Equipment |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Outpatient Bldg Light | Lighting |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Reference Buildings
Outpatient Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Outpatient Bldg Light | Lighting |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient Bldg Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient Bldg Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Outpatient ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Reference Buildings
Outpatient ClgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 25 | From DOE Reference Buildings
Outpatient ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Reference Buildings
Outpatient Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Outpatient Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
Outpatient Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Outpatient Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
Outpatient HtgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Reference Buildings
Outpatient HtgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 18.3 | From DOE Reference Buildings
Outpatient HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Reference Buildings
Outpatient Infil | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
Outpatient Infil | Infiltration |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Outpatient OR ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | From DOE Reference Buildings
Outpatient OR HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 18.3 | From DOE Reference Buildings
Outpatient Radiology Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | From DOE Reference Buildings
Outpatient Radiology Equip | Equipment |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.01 | From DOE Reference Buildings
Outpatient Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
OutPatientHealthCare AHU-1_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OutPatientHealthCare AHU-1_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OutPatientHealthCare AHU-1_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.33 | From DOE Prototype Buildings
OutPatientHealthCare AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OutPatientHealthCare ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OutPatientHealthCare BLDG_CAV_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_CAV_SCH_HUMID | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_ELEVATORS | Elevator |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OutPatientHealthCare BLDG_ELEVATORS | Elevator |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH | Equipment |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH | Equipment |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH_BASE | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH_BASE | Equipment |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH_BASE | Equipment |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_TOILET_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_TOILET_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_TOILET_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OA_FRAC_SCH | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OA_FRAC_SCH | OA Air |  | WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OA_SCH | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OA_SCH | OA Air |  | WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OCC_SCH | Occupancy |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OCC_SCH | Occupancy |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | From DOE Prototype Buildings
OutPatientHealthCare CAV_SAT_SCH | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 11.1 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 22.2 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 23.9 | 23.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 23.9 | 23.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
OutPatientHealthCare CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OutPatientHealthCare CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OutPatientHealthCare CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OutPatientHealthCare CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OutPatientHealthCare CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 6.7 | From DOE Prototype Buildings
OutPatientHealthCare Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
OutPatientHealthCare Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OutPatientHealthCare Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OutPatientHealthCare Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OutPatientHealthCare FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OutPatientHealthCare Floor 1 Anesthesia Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Anesthesia Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Anesthesia Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Anesthesia Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Control Room Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Control Room Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Control Room Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Control Room Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Room Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Room Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Room Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Room Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 1 humidity sched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 1 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 1 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 1 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 1 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 2 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 2 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 2 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 2 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 PACU Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 PACU Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 PACU Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 PACU Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 1 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 1 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 1 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 1 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 2 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 2 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 2 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 2 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Procedure Room Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Procedure Room Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Procedure Room Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Procedure Room Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Recovery Room Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Recovery Room Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Recovery Room Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Recovery Room Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Step Down Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Step Down Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Step Down Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Step Down Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare Floor 2 X-Ray Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OutPatientHealthCare Floor 2 X-Ray Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Floor 2 X-Ray Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare Floor 2 X-Ray Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 1 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 1 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 1 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 1 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 2 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 2 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 2 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 2 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 16 | From DOE Prototype Buildings
OutPatientHealthCare HeatSys1 Loop Setpoint Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 82.2 | From DOE Prototype Buildings
OutPatientHealthCare Hours_of_operation | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 18.3 | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 18.3 | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 19.4 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Prototype Buildings
OutPatientHealthCare Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 50 | From DOE Prototype Buildings
OutPatientHealthCare HVACOperationSchd | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OutPatientHealthCare HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OutPatientHealthCare INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OutPatientHealthCare INFIL_HALF_ON_SCH | Infiltration |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
OutPatientHealthCare INFIL_HALF_ON_SCH | Infiltration |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OutPatientHealthCare INFIL_SCH | Infiltration |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.25 | From DOE Prototype Buildings
OutPatientHealthCare INFIL_SCH | Infiltration |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OutPatientHealthCare MaxRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare MinOA_MotorizedDamper_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OutPatientHealthCare MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OutPatientHealthCare MinRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 40 | From DOE Prototype Buildings
OutPatientHealthCare MinRelHumSetSch_addDI | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
OutPatientHealthCare OR_CLGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | From DOE Prototype Buildings
OutPatientHealthCare OR_HTGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 18.3 | From DOE Prototype Buildings
OutPatientHealthCare OR_MinSA_Sched | Unknown |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
OutPatientHealthCare OR_MinSA_Sched | Unknown |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
OutPatientHealthCare OR_MinSA_Sched | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OutPatientHealthCare PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
OutPatientHealthCare ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
OutPatientHealthCare Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 11.1 | From DOE Prototype Buildings
OutPatientHealthCare SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
OutPatientHealthCare SWHSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 22 | From DOE Prototype Buildings
OutPatientHealthCare SWHSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare SWHSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
OutPatientHealthCare VAV_SAT_SCH | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 12.8 | From DOE Prototype Buildings
OutPatientHealthCare WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
PrimarySchool BathCorrMechKitchen ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 27 | From DOE Reference Buildings
PrimarySchool BathCorrMechKitchen ClgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
PrimarySchool BathCorrMechKitchen HtgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 16 | From DOE Reference Buildings
PrimarySchool BathCorrMechKitchen HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0.35 | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.25 | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.35 | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.35 | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool ClgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
PrimarySchool ClgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Reference Buildings
PrimarySchool ClgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
PrimarySchool ClgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 27 | 27 | From DOE Reference Buildings
PrimarySchool ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 27 | From DOE Reference Buildings
PrimarySchool Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 1.1 | From DOE Reference Buildings
PrimarySchool Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.6 | From DOE Reference Buildings
PrimarySchool Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | Hr 1: 1.1 | From DOE Reference Buildings
PrimarySchool Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | Hr 1: 0.6 | From DOE Reference Buildings
PrimarySchool Exterior Lights | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
PrimarySchool Exterior Lights Always On | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | bar: Hr 1 to Hr 24
PrimarySchool Gym Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
PrimarySchool HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 16 | From DOE Reference Buildings
PrimarySchool HtgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
PrimarySchool HtgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16 | From DOE Reference Buildings
PrimarySchool HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Reference Buildings
PrimarySchool Infil | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13 | 0.13 | 0.2 | 0.2 | 0.2 | 0.13 | 0.13 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0.1 | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1 | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1 | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1 | From DOE Reference Buildings
PrimarySchool Kitchen Exhaust | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Kitchen Exhaust | Equipment |  | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0.02 | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.02 | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.02 | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.02 | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
PrimarySchool PSZ-AC OA Damper | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
PrimarySchool PSZ-AC OA Damper | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0
PrimarySchool PSZ-AC Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
PrimarySchool PSZ-AC Operation | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0
PrimarySchool VAV OA Damper | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
PrimarySchool VAV OA Damper | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0
PrimarySchool VAV Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
PrimarySchool VAV Operation | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0
PrimarySchool Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Equip | Equipment |  | Default¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.35 | 0.35 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.35 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
QuickServiceRestaurant Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.3 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.2 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
QuickServiceRestaurant Bldg Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.2 | 0.45 | 0.6 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.2 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Swh | Service Water Heating |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Swh | Service Water Heating |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Swh | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | From DOE Reference Buildings
QuickServiceRestaurant ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Reference Buildings
QuickServiceRestaurant ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Reference Buildings
QuickServiceRestaurant ClgSetp Kitchen | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Reference Buildings
QuickServiceRestaurant ClgSetp Kitchen | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Reference Buildings
QuickServiceRestaurant Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
QuickServiceRestaurant Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
QuickServiceRestaurant Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
QuickServiceRestaurant Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
QuickServiceRestaurant Gas Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.09 | 0.14 | 0.1 | 0.1 | 0.22 | 0.27 | 0.24 | 0.21 | 0.14 | 0.13 | 0.15 | 0.17 | 0.17 | 0.17 | 0.15 | 0.14 | 0.12 | 0.02 | From DOE Reference Buildings
QuickServiceRestaurant Gas Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.25 | From DOE Reference Buildings
QuickServiceRestaurant Gas Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 19 | From DOE Reference Buildings
QuickServiceRestaurant Infil Half On | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
QuickServiceRestaurant Kitchen Exhaust | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
QuickServiceRestaurant Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
RestaurantFastFood AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
RestaurantFastFood ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantFastFood ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantFastFood BLDG_EQUIP_SCH | Equipment |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03 | From DOE Prototype Buildings
RestaurantFastFood BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.29 | From DOE Prototype Buildings
RestaurantFastFood BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2010 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.19034 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.28551 | 0.28551 | 0.47585 | 0.47585 | 0.66619 | 0.66619 | 0.66619 | 0.66619 | 0.66619 | 0.66619 | 0.57102 | 0.57102 | 0.57102 | 0.57102 | 0.57102 | 0.57102 | 0.47585 | 0.28551 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2010 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.19034 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.28551 | 0.28551 | 0.57102 | 0.57102 | 0.76136 | 0.76136 | 0.76136 | 0.76136 | 0.76136 | 0.76136 | 0.76136 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.47585 | 0.28551 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2010 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2010 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.14275 | 0.15 | 0.15 | 0.15 | 0.15 | 0.19034 | 0.38068 | 0.38068 | 0.57102 | 0.57102 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.47585 | 0.28551 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2010 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2013 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1865 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2797 | 0.2797 | 0.4662 | 0.4662 | 0.6527 | 0.6527 | 0.6527 | 0.6527 | 0.6527 | 0.6527 | 0.5594 | 0.5594 | 0.5594 | 0.5594 | 0.5594 | 0.5594 | 0.4662 | 0.2797 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2013 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1865 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2797 | 0.2797 | 0.5594 | 0.5594 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.4662 | 0.2797 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2013 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2013 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1399 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1865 | 0.373 | 0.373 | 0.5594 | 0.5594 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.4662 | 0.2797 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2013 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2004_2007 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2004_2007 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2004_2007 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2004_2007 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2004_2007 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2010_2013 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.17776 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.26664 | 0.26664 | 0.4444 | 0.4444 | 0.62216 | 0.62216 | 0.62216 | 0.62216 | 0.62216 | 0.62216 | 0.53328 | 0.53328 | 0.53328 | 0.53328 | 0.53328 | 0.53328 | 0.4444 | 0.26664 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2010_2013 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.17776 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.26664 | 0.26664 | 0.53328 | 0.53328 | 0.71104 | 0.71104 | 0.71104 | 0.71104 | 0.71104 | 0.71104 | 0.71104 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.4444 | 0.26664 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2010_2013 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2010_2013 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.13332 | 0.15 | 0.15 | 0.15 | 0.15 | 0.17776 | 0.35552 | 0.35552 | 0.53328 | 0.53328 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.4444 | 0.26664 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2010_2013 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantFastFood BLDG_LIGHT_SCH | Lighting |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantFastFood BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2 | From DOE Prototype Buildings
RestaurantFastFood BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35 | From DOE Prototype Buildings
RestaurantFastFood BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantFastFood BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | From DOE Prototype Buildings
RestaurantFastFood BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantFastFood BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.1 | 0.72 | 0.6 | 0.98 | 0.92 | 0.25 | 0.25 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0 | From DOE Prototype Buildings
RestaurantFastFood BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.33 | 0.13 | 0.1 | 0.72 | 0.31 | 0.98 | 0.92 | 0.22 | 0.31 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0.15 | From DOE Prototype Buildings
RestaurantFastFood BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.1 | 0.72 | 0.6 | 0.98 | 0.92 | 0.25 | 0.25 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0.15 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 28.33 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.11 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 28.33 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 28.9 | 27.8 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 28.33 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 23.89 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
RestaurantFastFood CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
RestaurantFastFood CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantFastFood CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RestaurantFastFood CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RestaurantFastFood DOOR_INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.258 | 0.258 | 0.363 | 0.558 | 0.558 | 0.363 | 0.258 | 0.363 | 0.462 | 0.558 | 0.65 | 0.74 | 0.462 | 0.258 | 0.258 | From DOE Prototype Buildings
RestaurantFastFood DOOR_INFIL_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.462 | 0.258 | 0.462 | 0.558 | 0.558 | 0.462 | 0.363 | 0.363 | 0.363 | 0.74 | 0.915 | 0.74 | 0.65 | 0.558 | 0.363 | From DOE Prototype Buildings
RestaurantFastFood DOOR_INFIL_SCH | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantFastFood DOOR_INFIL_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.462 | 0.462 | 0.462 | 0.258 | 0.558 | 0.829 | 0.74 | 0.462 | 0.258 | 0.363 | 0.558 | 0.829 | 0.829 | 0.829 | 0.558 | 0.363 | 0.258 | From DOE Prototype Buildings
RestaurantFastFood DOOR_INFIL_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantFastFood Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
RestaurantFastFood Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RestaurantFastFood Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantFastFood FF_GAS_EQUIP_SCH | Equipment |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03 | From DOE Prototype Buildings
RestaurantFastFood FF_GAS_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.29 | From DOE Prototype Buildings
RestaurantFastFood FF_GAS_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantFastFood Hours_of_operation | Operation |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.22 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 16.7 | 17.8 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.22 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RestaurantFastFood HVACOperationSchd | Operation |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood INFIL_SCH_PNNL | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
RestaurantFastFood Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule_2004 | Equipment |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.53051 | 0 | 0 | 0 | 0 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | From DOE Prototype Buildings
RestaurantFastFood Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule_2007_2010_2013 | Equipment |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.53051 | 0 | 0 | 0 | 0 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | From DOE Prototype Buildings
RestaurantFastFood Kitchen Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
RestaurantFastFood Kitchen Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
RestaurantFastFood Kitchen Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
RestaurantFastFood Kitchen Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
RestaurantFastFood Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RestaurantFastFood Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
RestaurantFastFood Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RestaurantFastFood Kitchen_Exhaust_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood MinOA_FFKitch_Sched | OA Air |  | Default¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood MinOA_FFKitch_Sched | OA Air |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RestaurantFastFood MinOA_MotorizedDamper_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RestaurantFastFood PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantFastFood SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantFastFood SHWSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 22 | From DOE Prototype Buildings
RestaurantFastFood SHWSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
RestaurantFastFood SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.241 | 0.241 | 0.345 | 0.542 | 0.542 | 0.345 | 0.241 | 0.345 | 0.445 | 0.542 | 0.637 | 0.73 | 0.445 | 0.241 | 0.241 | From DOE Prototype Buildings
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.445 | 0.241 | 0.445 | 0.542 | 0.542 | 0.445 | 0.345 | 0.345 | 0.345 | 0.73 | 0.911 | 0.73 | 0.637 | 0.542 | 0.345 | From DOE Prototype Buildings
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.445 | 0.445 | 0.445 | 0.241 | 0.542 | 0.821 | 0.73 | 0.445 | 0.241 | 0.345 | 0.542 | 0.821 | 0.821 | 0.821 | 0.542 | 0.345 | 0.241 | From DOE Prototype Buildings
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantFastFood walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.156 | 0.156 | 0.26 | 0.26 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.26 | 0.156 | From DOE Prototype Buildings
RestaurantFastFood walkin_occ_lght_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.156 | 0.156 | 0.312 | 0.312 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.26 | 0.156 | From DOE Prototype Buildings
RestaurantFastFood walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantFastFood walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.104 | 0.208 | 0.208 | 0.312 | 0.312 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.26 | 0.156 | From DOE Prototype Buildings
RestaurantFastFood walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantFastFood WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantSitDown AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
RestaurantSitDown ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantSitDown ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantSitDown BLDG_EQUIP_SCH | Equipment |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03 | From DOE Prototype Buildings
RestaurantSitDown BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.29 | From DOE Prototype Buildings
RestaurantSitDown BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantSitDown BLDG_LIGHT_DINING_SCH | Lighting |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | Lighting |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantSitDown BLDG_LIGHT_SCH | Lighting |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantSitDown BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2 | From DOE Prototype Buildings
RestaurantSitDown BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35 | From DOE Prototype Buildings
RestaurantSitDown BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantSitDown BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | From DOE Prototype Buildings
RestaurantSitDown BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantSitDown BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | From DOE Prototype Buildings
RestaurantSitDown BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | From DOE Prototype Buildings
RestaurantSitDown BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown Booster Water Inlet Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
RestaurantSitDown Booster Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 82.22 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 28.9 | 27.8 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
RestaurantSitDown CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
RestaurantSitDown CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantSitDown CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RestaurantSitDown CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RestaurantSitDown CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantSitDown DOOR_INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.258 | 0.258 | 0.363 | 0.558 | 0.558 | 0.363 | 0.258 | 0.363 | 0.462 | 0.558 | 0.65 | 0.74 | 0.462 | 0.258 | 0.258 | From DOE Prototype Buildings
RestaurantSitDown DOOR_INFIL_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.462 | 0.258 | 0.462 | 0.558 | 0.558 | 0.462 | 0.363 | 0.363 | 0.363 | 0.74 | 0.915 | 0.74 | 0.65 | 0.558 | 0.363 | From DOE Prototype Buildings
RestaurantSitDown DOOR_INFIL_SCH | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RestaurantSitDown DOOR_INFIL_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.462 | 0.462 | 0.462 | 0.258 | 0.558 | 0.829 | 0.74 | 0.462 | 0.258 | 0.363 | 0.558 | 0.829 | 0.829 | 0.829 | 0.558 | 0.363 | 0.258 | From DOE Prototype Buildings
RestaurantSitDown DOOR_INFIL_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantSitDown Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
RestaurantSitDown Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantSitDown Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RestaurantSitDown Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 16 | From DOE Prototype Buildings
RestaurantSitDown Hours_of_operation | Operation |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 19 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 19 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 19 | 15.6 | 15.6 | 15.6 | 16.7 | 17.8 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 19 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
RestaurantSitDown Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 50 | From DOE Prototype Buildings
RestaurantSitDown HVACOperationSchd | Operation |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown INFIL_HALF_ON_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
RestaurantSitDown INFIL_SCH_PNNL | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
RestaurantSitDown Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.93371 | 0 | 0 | 0 | 0 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | From DOE Prototype Buildings
RestaurantSitDown Kitchen Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
RestaurantSitDown Kitchen Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
RestaurantSitDown Kitchen Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
RestaurantSitDown Kitchen Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
RestaurantSitDown Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RestaurantSitDown Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
RestaurantSitDown Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantSitDown Kitchen_Exhaust_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown MaxRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
RestaurantSitDown MinOA_FFKitch_Sched | OA Air |  | Default¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | From DOE Prototype Buildings
RestaurantSitDown MinOA_FFKitch_Sched | OA Air |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.65 | From DOE Prototype Buildings
RestaurantSitDown MinOA_MotorizedDamper_Sched | OA Air |  | Default¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RestaurantSitDown MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantSitDown MinOA_SDKitch_Sched | OA Air |  | Default¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown MinOA_SDKitch_Sched | OA Air |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantSitDown MinRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Prototype Buildings
RestaurantSitDown PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantSitDown Rest_GAS_EQUIP_SCH | Equipment |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03 | From DOE Prototype Buildings
RestaurantSitDown Rest_GAS_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.29 | From DOE Prototype Buildings
RestaurantSitDown Rest_GAS_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantSitDown Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
RestaurantSitDown Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
RestaurantSitDown Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
RestaurantSitDown SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantSitDown SWHSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 22 | From DOE Prototype Buildings
RestaurantSitDown SWHSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
RestaurantSitDown SWHSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.241 | 0.241 | 0.345 | 0.542 | 0.542 | 0.345 | 0.241 | 0.345 | 0.445 | 0.542 | 0.637 | 0.73 | 0.445 | 0.241 | 0.241 | From DOE Prototype Buildings
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.445 | 0.241 | 0.445 | 0.542 | 0.542 | 0.445 | 0.345 | 0.345 | 0.345 | 0.73 | 0.911 | 0.73 | 0.637 | 0.542 | 0.345 | From DOE Prototype Buildings
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.445 | 0.445 | 0.445 | 0.241 | 0.542 | 0.821 | 0.73 | 0.445 | 0.241 | 0.345 | 0.542 | 0.821 | 0.821 | 0.821 | 0.542 | 0.345 | 0.241 | From DOE Prototype Buildings
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantSitDown walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.156 | 0.156 | 0.312 | 0.312 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.26 | 0.156 | From DOE Prototype Buildings
RestaurantSitDown walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RestaurantSitDown walkin_occ_lght_SCH | Occupancy |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.156 | 0.156 | 0.26 | 0.26 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.26 | 0.156 | From DOE Prototype Buildings
RestaurantSitDown walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RestaurantSitDown WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Retail Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | From DOE Reference Buildings
Retail Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | From DOE Reference Buildings
Retail Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Retail Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | From DOE Reference Buildings
Retail Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Retail Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
Retail Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
Retail Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Retail Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Retail Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Retail Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | From DOE Reference Buildings
Retail Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | From DOE Reference Buildings
Retail Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Retail Bldg Occ | Occupancy |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Retail ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | From DOE Reference Buildings
Retail ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | From DOE Reference Buildings
Retail ClgSetp | Thermostat Setpoint | C | Sun | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
Retail ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Reference Buildings
Retail Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Retail Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
Retail Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Retail Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
Retail FRONT ENTRY COOLING | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 90 | From DOE Reference Buildings
Retail HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Retail HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
Retail HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Reference Buildings
Retail HtgSetp | Thermostat Setpoint | C | Sun | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Retail HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Reference Buildings
Retail INFIL FRONT | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
Retail INFIL FRONT | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | From DOE Reference Buildings
Retail INFIL FRONT | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
Retail INFIL FRONT | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Retail Infil Half On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Reference Buildings
Retail Infil Half On | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | From DOE Reference Buildings
Retail Infil Half On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
Retail Infil Half On | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Retail Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
RetailStandalone AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
RetailStandalone ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStandalone ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RetailStandalone BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_ELEVATORS | Elevator |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_ELEVATORS | Elevator |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | From DOE Prototype Buildings
RetailStandalone BLDG_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | From DOE Prototype Buildings
RetailStandalone BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RetailStandalone BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
RetailStandalone BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RetailStandalone BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStandalone BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH_2010 | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH_2010 | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH_2010 | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RetailStandalone BLDG_OCC_SCH_2010 | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH_2010 | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStandalone BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 23.89 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
RetailStandalone CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
RetailStandalone CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RetailStandalone CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStandalone CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStandalone CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RetailStandalone CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 6.7 | From DOE Prototype Buildings
RetailStandalone Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
RetailStandalone Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
RetailStandalone Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RetailStandalone Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStandalone FRONT_ENTRY_COOLING | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 100 | From DOE Prototype Buildings
RetailStandalone FrontEntry_CoilSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RetailStandalone FrontEntry_FanSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStandalone Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 16 | From DOE Prototype Buildings
RetailStandalone Hot Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
RetailStandalone Hours_of_operation | Operation |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone Hours_of_operation | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone Hours_of_operation | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_FrontEntry_STD2013 | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_FrontEntry_STD2013 | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_FrontEntry_STD2013 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_FrontEntry_STD2013 | Thermostat Setpoint | C | WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 50 | From DOE Prototype Buildings
RetailStandalone HVACOperationSchd | Operation |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone HVACOperationSchd | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone HVACOperationSchd | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
RetailStandalone INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone INFIL_HALF_ON_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_HALF_ON_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_HALF_ON_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_HALF_ON_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStandalone INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStandalone INFIL_SCH_PNNL | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH_PNNL | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH_PNNL | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone MinOA_MotorizedDamper_Sched | OA Air |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone MinOA_MotorizedDamper_Sched | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RetailStandalone MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStandalone PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RetailStandalone ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStandalone Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
RetailStandalone Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
RetailStandalone Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
RetailStandalone SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStandalone WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStripmall AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
RetailStripmall ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStripmall CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
RetailStripmall CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RetailStripmall CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStripmall CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStripmall Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
RetailStripmall Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RetailStripmall Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Hot Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
RetailStripmall INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Fri¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
RetailStripmall Type1_EQUIP_SCH | Equipment |  | Default¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | From DOE Prototype Buildings
RetailStripmall Type1_EQUIP_SCH | Equipment |  | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | From DOE Prototype Buildings
RetailStripmall Type1_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
RetailStripmall Type1_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStripmall Type1_FAN_SCH | Unknown |  | Default¦SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type1_FAN_SCH | Unknown |  | WntrDsn¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RetailStripmall Type1_Infil_SCH | Infiltration |  | Default¦SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
RetailStripmall Type1_Infil_SCH | Infiltration |  | WntrDsn¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
RetailStripmall Type1_LIGHT_SCH | Lighting |  | Default¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | From DOE Prototype Buildings
RetailStripmall Type1_LIGHT_SCH | Lighting |  | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | From DOE Prototype Buildings
RetailStripmall Type1_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStripmall Type1_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStripmall Type1_MinOA_MotorizedDamper_SCH | OA Air |  | Default¦SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type1_MinOA_MotorizedDamper_SCH | OA Air |  | WntrDsn¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type1_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.6 | 0.4 | 0.4 | 0.3 | 0.6 | 0.6 | 0.4 | 0.4 | 0.3 | 0.2 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type1_OCC_SCH | Occupancy |  | Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type1_OCC_SCH | Occupancy |  | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.2 | 0.6 | 0.4 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.2 | From DOE Prototype Buildings
RetailStripmall Type1_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStripmall Type1_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStripmall Type1_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.16 | 0.1 | From DOE Prototype Buildings
RetailStripmall Type1_SWH_SCH | Service Water Heating |  | SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.62 | 0.6 | 0.55 | 0.45 | 0.5 | 0.46 | 0.47 | 0.34 | 0.33 | 0.23 | 0.13 | From DOE Prototype Buildings
RetailStripmall Type1_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.23 | 0.32 | 0.41 | 0.65 | 0.6 | 0.55 | 0.45 | 0.5 | 0.46 | 0.47 | 0.34 | 0.33 | 0.23 | 0.13 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 23.89 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStripmall Type2_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStripmall Type2_FAN_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_FAN_SCH | Unknown |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_FAN_SCH | Unknown |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_Infil_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type2_Infil_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type2_Infil_SCH | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type2_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStripmall Type2_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStripmall Type2_MinOA_MotorizedDamper_SCH | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_MinOA_MotorizedDamper_SCH | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_MinOA_MotorizedDamper_SCH | OA Air |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.2 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.4 | 0.3 | 0.3 | 0.3 | 0.05 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStripmall Type2_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.3 | 0.2 | 0.2 | 0.5 | 0.5 | 0.2 | 0.05 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStripmall Type2_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.14 | 0.29 | 0.33 | 0.4 | 0.36 | 0.37 | 0.35 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.62 | 0.6 | 0.5 | 0.48 | 0.47 | 0.34 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 23.89 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStripmall Type3_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStripmall Type3_FAN_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_FAN_SCH | Unknown |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_FAN_SCH | Unknown |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_Infil_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type3_Infil_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type3_Infil_SCH | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type3_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStripmall Type3_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStripmall Type3_MinOA_MotorizedDamper_SCH | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_MinOA_MotorizedDamper_SCH | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_MinOA_MotorizedDamper_SCH | OA Air |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.43 | 0.46 | 0.5 | 0.69 | 0.34 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.58 | 0.71 | 0.74 | 0.77 | 0.8 | 0.74 | 0.54 | 0.11 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
RetailStripmall Type3_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.43 | 0.46 | 0.71 | 0.5 | 0.69 | 0.54 | 0.71 | 0.34 | 0.26 | 0.11 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
RetailStripmall Type3_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.25 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Schedule:Compact 1 | Unknown |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Reference Buildings
Schedule:Compact 1 | Unknown |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Schedule:Compact 1 | Unknown |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
SchoolPrimary AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
SchoolPrimary ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolPrimary Bath_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
SchoolPrimary Bath_ZN_1_FLR_1 SHW_default Latent fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
SchoolPrimary Bath_ZN_1_FLR_1 SHW_default Sensible fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
SchoolPrimary Bath_ZN_1_FLR_1 SHW_default Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.35 | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.25 | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.35 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-09-16 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-06-16 | 2014-09-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Wknd | 2014-06-16 | 2014-09-15 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Wknd | 2014-01-01 | 2014-06-15 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Sat | 2014-09-16 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Sun¦Sat | 2014-06-16 | 2014-09-15 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Sun¦Sat | 2014-01-01 | 2014-06-15 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-09-16 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-06-16 | 2014-09-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-01-01 | 2014-06-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | From DOE Prototype Buildings
SchoolPrimary Booster Water Inlet Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
SchoolPrimary Booster Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 82.22 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_Setup | Thermostat Setpoint | C | Default¦WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_Setup | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.6 | From DOE Prototype Buildings
SchoolPrimary CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | Hr 1: 1.1 | From DOE Prototype Buildings
SchoolPrimary CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | Hr 1: 1.1 | From DOE Prototype Buildings
SchoolPrimary CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 1.1 | From DOE Prototype Buildings
SchoolPrimary CoolingCoilAvailSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolPrimary CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 6.7 | From DOE Prototype Buildings
SchoolPrimary Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
SchoolPrimary Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
SchoolPrimary Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolPrimary Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolPrimary Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolPrimary FAN_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolPrimary Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 16 | From DOE Prototype Buildings
SchoolPrimary Hours_of_operation | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary Hours_of_operation | Operation |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_Setback | Thermostat Setpoint | C | Default¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_Setback | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
SchoolPrimary Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 65 | From DOE Prototype Buildings
SchoolPrimary HVACOperationSchd | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary HVACOperationSchd | Operation |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 82 | From DOE Prototype Buildings
SchoolPrimary INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary INFIL_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolPrimary INFIL_SCH_PNNL | Infiltration |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolPrimary INFIL_SCH_PNNL | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1 | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.02 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.02 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.02 | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary MinOA_Kitchen_Sched | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary MinOA_Kitchen_Sched | Equipment |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolPrimary PlantOnSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolPrimary ReheatCoilAvailSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolPrimary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
SchoolPrimary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
SchoolPrimary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
SchoolPrimary SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary SHWSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 22 | From DOE Prototype Buildings
SchoolPrimary SHWSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
SchoolPrimary SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
SchoolPrimary VAV-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 12.8 | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolPrimary WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
SchoolSecondary ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolSecondary Bathrooms_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_1 SHW_default Latent fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_1 SHW_default Sensible fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_1 SHW_default Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_2 SHW_default Hot Supply Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_2 SHW_default Latent fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_2 SHW_default Sensible fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_2 SHW_default Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
SchoolSecondary BLDG_ELEVATORS | Elevator |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.3 | From DOE Prototype Buildings
SchoolSecondary BLDG_ELEVATORS | Elevator |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.35 | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.25 | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.35 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-09-16 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-06-16 | 2014-09-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Wknd | 2014-06-16 | 2014-09-15 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Wknd | 2014-01-01 | 2014-06-15 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Sat | 2014-09-16 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Sun¦Sat | 2014-06-16 | 2014-09-15 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Sun¦Sat | 2014-01-01 | 2014-06-15 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-09-16 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-06-16 | 2014-09-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-01-01 | 2014-06-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | From DOE Prototype Buildings
SchoolSecondary Booster Water Inlet Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
SchoolSecondary Booster Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 82.22 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_Setback | Thermostat Setpoint | C | Default¦WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_Setback | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
SchoolSecondary CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.6 | From DOE Prototype Buildings
SchoolSecondary CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | Hr 1: 1.1 | From DOE Prototype Buildings
SchoolSecondary CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | Hr 1: 1.1 | From DOE Prototype Buildings
SchoolSecondary CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 1.1 | From DOE Prototype Buildings
SchoolSecondary CoolingCoilAvailSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolSecondary CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 6.7 | From DOE Prototype Buildings
SchoolSecondary Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
SchoolSecondary ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolSecondary ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.3 | From DOE Prototype Buildings
SchoolSecondary ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
SchoolSecondary Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolSecondary Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolSecondary Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolSecondary FAN_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolSecondary Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 16 | From DOE Prototype Buildings
SchoolSecondary Hours_of_operation | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary Hours_of_operation | Operation |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_Setback | Thermostat Setpoint | C | Default¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_Setback | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Prototype Buildings
SchoolSecondary Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 65 | From DOE Prototype Buildings
SchoolSecondary HVACOperationSchd | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary HVACOperationSchd | Operation |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 82 | From DOE Prototype Buildings
SchoolSecondary INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary INFIL_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolSecondary INFIL_SCH_PNNL | Infiltration |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolSecondary INFIL_SCH_PNNL | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH_DCV | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.02 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.02 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.02 | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 55 | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.2 | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolSecondary PlantOnSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolSecondary ReheatCoilAvailSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
SchoolSecondary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
SchoolSecondary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
SchoolSecondary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | Hr 1: 13 | From DOE Prototype Buildings
SchoolSecondary SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary SHWSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 22 | From DOE Prototype Buildings
SchoolSecondary SHWSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
SchoolSecondary SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
SchoolSecondary VAV-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 12.8 | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SchoolSecondary WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool BLDG ELEVATORS | Elevator |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool BLDG ELEVATORS | Elevator |  | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0.35 | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.25 | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.35 | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.35 | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1773 | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1773 | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1773 | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool ClgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
SecondarySchool ClgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Reference Buildings
SecondarySchool ClgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
SecondarySchool ClgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 27 | 27 | From DOE Reference Buildings
SecondarySchool ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 27 | From DOE Reference Buildings
SecondarySchool ClgSetp BathCorrMechKitchen | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 27 | From DOE Reference Buildings
SecondarySchool ClgSetp BathCorrMechKitchen | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
SecondarySchool Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 1.1 | From DOE Reference Buildings
SecondarySchool Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.6 | From DOE Reference Buildings
SecondarySchool Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | Hr 1: 1.1 | From DOE Reference Buildings
SecondarySchool Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | Hr 1: 0.6 | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Exterior Lights | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SecondarySchool Exterior Lights Always On | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | bar: Hr 1 to Hr 24
SecondarySchool Gym Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
SecondarySchool HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 16 | From DOE Reference Buildings
SecondarySchool HtgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
SecondarySchool HtgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16 | From DOE Reference Buildings
SecondarySchool HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Reference Buildings
SecondarySchool HtgSetp BathCorrMechKitchen | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 16 | From DOE Reference Buildings
SecondarySchool HtgSetp BathCorrMechKitchen | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
SecondarySchool Infil | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13 | 0.13 | 0.2 | 0.2 | 0.2 | 0.13 | 0.13 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0.1 | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.1 | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.1 | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1 | From DOE Reference Buildings
SecondarySchool Kitchen Exhaust | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Kitchen Exhaust | Equipment |  | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0.02 | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0.02 | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0.02 | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.02 | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SecondarySchool PSZ-AC OA Damper | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
SecondarySchool PSZ-AC OA Damper | Operation | Dimensionless | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
SecondarySchool PSZ-AC OA Damper | Operation | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0
SecondarySchool PSZ-AC Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
SecondarySchool PSZ-AC Operation | Operation | Dimensionless | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
SecondarySchool PSZ-AC Operation | Operation | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0
SecondarySchool VAV OA Damper | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
SecondarySchool VAV OA Damper | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0
SecondarySchool VAV Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
SecondarySchool VAV Operation | Operation | Dimensionless | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
SecondarySchool VAV Operation | Operation | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0
SecondarySchool Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Small Office Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Reference Buildings
Small Office Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Small Office Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Small Office Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.3 | From DOE Reference Buildings
Small Office Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Small Office Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | From DOE Reference Buildings
Small Office Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Small Office Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Small Office Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.05 | From DOE Reference Buildings
Small Office Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Small Office Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Small Office Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Small Office Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Reference Buildings
Small Office Bldg Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Small Office ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Reference Buildings
Small Office ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Reference Buildings
Small Office ClgSetp | Thermostat Setpoint | C | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Reference Buildings
Small Office Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Small Office Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
Small Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Small Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
Small Office HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
Small Office HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Small Office HtgSetp | Thermostat Setpoint | C | SmrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Reference Buildings
Small Office HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Reference Buildings
Small Office Infil Quarter On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Reference Buildings
Small Office Infil Quarter On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Small Office Infil Quarter On | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
Small Office Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel BLDG ELEVATORS | Elevator |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Reference Buildings
SmallHotel Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | From DOE Reference Buildings
SmallHotel Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | From DOE Reference Buildings
SmallHotel Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SmallHotel Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | From DOE Reference Buildings
SmallHotel Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Reference Buildings
SmallHotel Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Reference Buildings
SmallHotel Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
SmallHotel Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Reference Buildings
SmallHotel Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | From DOE Reference Buildings
SmallHotel Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | From DOE Reference Buildings
SmallHotel Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SmallHotel Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | From DOE Reference Buildings
SmallHotel Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 24 | From DOE Reference Buildings
SmallHotel Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SmallHotel Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
SmallHotel Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SmallHotel Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
SmallHotel Corridor Light | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SmallHotel Exercise Equip | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | From DOE Reference Buildings
SmallHotel Exercise Light | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | From DOE Reference Buildings
SmallHotel Exercise Occ | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | From DOE Reference Buildings
SmallHotel Exterior Lights | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | bar: Hr 1
SmallHotel GuestRoom Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Reference Buildings
SmallHotel GuestRoom Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SmallHotel GuestRoom Equip | Equipment |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Reference Buildings
SmallHotel GuestRoom Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel GuestRoom Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | From DOE Reference Buildings
SmallHotel GuestRoom Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SmallHotel GuestRoom Light | Lighting |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | From DOE Reference Buildings
SmallHotel GuestRoom Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel GuestRoom Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | From DOE Reference Buildings
SmallHotel GuestRoom Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SmallHotel GuestRoom Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
SmallHotel GuestRoom Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Reference Buildings
SmallHotel Infil | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
SmallHotel Infil Half On | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
SmallHotel Laundry Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Laundry Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
SmallHotel Laundry Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel Laundry Gas | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Laundry Gas | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SmallHotel Laundry Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel Laundry Light | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Laundry Occ | Occupancy |  | Default¦Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Laundry Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SmallHotel Laundry Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel Meeting Equip | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Meeting Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | From DOE Reference Buildings
SmallHotel Meeting Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SmallHotel Meeting Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel Meeting Occ | Occupancy |  | Default¦Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Meeting Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
SmallHotel Meeting Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel Office Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Reference Buildings
SmallHotel Office Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SmallHotel Office Equip | Equipment |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Reference Buildings
SmallHotel Office Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel Office Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
SmallHotel Office Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SmallHotel Office Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel Office Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Reference Buildings
SmallHotel Office Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
SmallHotel Office Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Reference Buildings
SmallHotel Office Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel PSZ-AC OA Damper | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | bar: Hr 1
SmallHotel PSZ-AC Operation | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | bar: Hr 1 to Hr 24
SmallHotel PTAC OA Damper | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0
SmallHotel PTAC Operation | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | bar: Hr 1 to Hr 24
SmallHotel Split-AC OA Damper | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | bar: Hr 1
SmallHotel Split-AC Operation | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | bar: Hr 1 to Hr 24
SmallHotel StaffLounge Equip | Equipment |  | Default¦Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | From DOE Reference Buildings
SmallHotel StaffLounge Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
SmallHotel StaffLounge Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel StaffLounge Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05 | From DOE Reference Buildings
SmallHotel StaffLounge Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SmallHotel StaffLounge Light | Lighting |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05 | From DOE Reference Buildings
SmallHotel StaffLounge Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel StaffLounge Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel StaffLounge Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SmallHotel StaffLounge Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel StaffLounge Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel Storage Light | Lighting |  | Default¦Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Reference Buildings
SmallHotel Storage Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SmallHotel Storage Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallHotel UnitHeater ClgSP Sch | Thermostat Setpoint |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 40 | From DOE Reference Buildings
SmallHotel UnitHeater HtgSP Sch | Thermostat Setpoint |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Reference Buildings
SmallHotel Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SmallOffice Exterior Lights | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SmallOffice Exterior Lights Always On | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | bar: Hr 1 to Hr 24
SmallOffice PSZ-AC OA Damper | Operation | Dimensionless | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
SmallOffice PSZ-AC OA Damper | Operation | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0
SmallOffice PSZ-AC Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
SmallOffice PSZ-AC Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
SmallOffice PSZ-AC Operation | Operation | Dimensionless | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0
StripMall Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | From DOE Reference Buildings
StripMall Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | From DOE Reference Buildings
StripMall Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
StripMall Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | From DOE Reference Buildings
StripMall Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
StripMall Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
StripMall Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
StripMall Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
StripMall Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
StripMall Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
StripMall Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | From DOE Reference Buildings
StripMall Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | From DOE Reference Buildings
StripMall Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
StripMall Bldg Occ | Occupancy |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
StripMall ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | From DOE Reference Buildings
StripMall ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | From DOE Reference Buildings
StripMall ClgSetp | Thermostat Setpoint | C | Sun | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
StripMall ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Reference Buildings
StripMall Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
StripMall Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
StripMall Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
StripMall Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
StripMall HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
StripMall HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
StripMall HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Reference Buildings
StripMall HtgSetp | Thermostat Setpoint | C | Sun | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
StripMall HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Reference Buildings
Stripmall HVACOperationSchd | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Stripmall HVACOperationSchd | Equipment |  | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
Stripmall HVACOperationSchd | Equipment |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
StripMall Infil Half On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Reference Buildings
StripMall Infil Half On | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | From DOE Reference Buildings
StripMall Infil Half On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
StripMall Infil Half On | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Stripmall MinOA_Sched | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Stripmall MinOA_Sched | Equipment |  | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
Stripmall MinOA_Sched | Equipment |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
StripMall Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SuperMarket Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | From DOE Reference Buildings
SuperMarket Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | From DOE Reference Buildings
SuperMarket Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SuperMarket Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.15 | 0.15 | From DOE Reference Buildings
SuperMarket Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SuperMarket Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
SuperMarket Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
SuperMarket Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
SuperMarket Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
SuperMarket Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SuperMarket Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0 | 0 | From DOE Reference Buildings
SuperMarket Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | From DOE Reference Buildings
SuperMarket Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SuperMarket Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | From DOE Reference Buildings
SuperMarket Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
SuperMarket Bldg Swh | Service Water Heating |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | From DOE Reference Buildings
SuperMarket Bldg Swh | Service Water Heating |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | From DOE Reference Buildings
SuperMarket Bldg Swh | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | From DOE Reference Buildings
SuperMarket ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | From DOE Reference Buildings
SuperMarket ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Reference Buildings
SuperMarket Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SuperMarket Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
SuperMarket Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
SuperMarket Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
SuperMarket HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
SuperMarket HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Reference Buildings
SuperMarket Infil Half On | Infiltration |  | Default¦SmrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | From DOE Reference Buildings
SuperMarket Infil Half On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
SuperMarket Infil Half On | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
SuperMarket Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Warehouse Always Off Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Warehouse Always On Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Warehouse ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Warehouse ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Warehouse Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Warehouse Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Warehouse Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Warehouse Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1 | From DOE Reference Buildings
Warehouse Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Warehouse Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Warehouse Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.24 | 0.24 | 0.24 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Warehouse Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1
Warehouse Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1 | From DOE Reference Buildings
Warehouse Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Warehouse Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Warehouse Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Warehouse Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Warehouse Bldg Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Warehouse BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.18 | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_OFFICE_SCH | Lighting |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.42 | 0.77 | 0.77 | 0.77 | 0.77 | 0.68 | 0.77 | 0.77 | 0.77 | 0.77 | 0.61 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Warehouse BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_STORAGE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.1 | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_STORAGE_SCH | Lighting |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.6 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_STORAGE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Warehouse BLDG_LIGHT_STORAGE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Warehouse BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Warehouse BLDG_OCC_SCH | Occupancy |  | WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.53 | 1 | 1 | 1 | 1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Warehouse Bulk Storage Heating Setpoint Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 10 | From DOE Prototype Buildings
Warehouse ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
Warehouse ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
Warehouse ClgSetp | Thermostat Setpoint | C | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 30 | From DOE Reference Buildings
Warehouse ClgSetp FineStorage | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Reference Buildings
Warehouse Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Warehouse Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
Warehouse Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | [24 empty] | From DOE Reference Buildings | bar: Hr 1 to Hr 24
Warehouse Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | Hr 1: 0.5 | From DOE Reference Buildings
Warehouse COMPACT HVAC-ALWAYS 1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Warehouse COMPACT HVAC-ALWAYS 4 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 4 | From DOE Prototype Buildings
Warehouse Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.5 | From DOE Prototype Buildings
Warehouse Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Warehouse Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
Warehouse Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
Warehouse Exterior_Ltg_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
Warehouse FanSched | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Warehouse FanSched | Unknown |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Warehouse FanSched | Unknown |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Warehouse Fine Storage Cooling Setpoint Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 26.7 | From DOE Prototype Buildings
Warehouse Fine Storage Heating Setpoint Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.56 | From DOE Prototype Buildings
Warehouse Hot Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 60 | From DOE Prototype Buildings
Warehouse HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | From DOE Reference Buildings
Warehouse HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | From DOE Reference Buildings
Warehouse HtgSetp | Thermostat Setpoint | C | SmrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.5 | From DOE Reference Buildings
Warehouse HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 21 | From DOE Reference Buildings
Warehouse HtgSetp BulkStorage | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 7.2 | From DOE Reference Buildings
Warehouse HtgSetp FineStorage | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 15.6 | From DOE Reference Buildings
Warehouse INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Warehouse INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Warehouse MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Warehouse MinOA_MotorizedDamper_Sched | OA Air |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Warehouse MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Warehouse MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Warehouse OA Damper Always ON Schedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Warehouse OA Damper Off during off hrs Schedule | OA Air |  | Default¦Sun | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Warehouse OA Damper Off during off hrs Schedule | OA Air |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Warehouse OA Damper Off during off hrs Schedule | OA Air |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1
Warehouse Office_Plug_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0.3 | From DOE Prototype Buildings
Warehouse Office_Plug_SCH | Unknown |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
Warehouse Office_Plug_SCH | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24
Warehouse Office_Plug_SCH | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Prototype Buildings
Warehouse Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | Hr 1: 0 | From DOE Reference Buildings
Warehouse ZoneControlSchedule | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | [24 empty] | From DOE Prototype Buildings | bar: Hr 1 to Hr 24